Director of Planning and Urban Development

Penny St. Louis Littell

INGRAHAM DAVID A B & DEBORAH			Certified 7003 3110 0002 6063 7179

9 Brookside Terrace

Veazie Maine   04401

CBL: 172  G007001

Located at 9 RAY ST

Dear INGRAHAM DAVID A B & DEBORAH R JTS,

An evaluation of the above-referenced property on 12/30/08   was performed for the

Legalization of a Nonconforming Dwelling Unit(s) as allowed under Sec. 14-391, The Land

Use Ordinance of the City of Portland.  The structure fails to comply with Chapter 6.Article

V. of the Code of Ordinances, The Housing Code.  Legalization of unit 3 requires that the

following :

- One (1) hard wired smoke detector in each bedroom and one (1) in the vicinity of the bedrooms in each unit, interconnected within the unit with battery backup.  Each Unit’s detectors must be interconnected with in the unit but independent from other dwellings units with in the structure.  All three units.  One hardwired smoke detector in basement. An electric permit is required.

- Hard wired smoke detectors in common areas interconnected.  3rd floor back hallway egress stairway, front hallway egress, and basement smoke detectors interconnected.  An electric permit is required. Per Fire Department

- Self closing 45 minute fire doors are required on second and third floor unit’s front doors.  Per Fire Department

- Unit one closet area wall (former stairway) must be sealed to prevent fire penetration. (2 layers of 5/8 type X sheetrock taped and fire caulked)

- Graspable Handrails on both sides of stairs from level two to level three.  Handrails must be continuous and returned at ends to wall or newell post.   Height required to be 34 to 38 inches measured from front edge of tread.

- Repair loose banister section on 2nd floor landing front

- Relief value drains on hot water heaters (basement) are required to end within 6 inches of the floor.

- Risers on egress stairs permit # 07-1198 open space must be less than 4 inches.

This is a notice of violation pursuant to Section 6-118 of the Code.  Within 30 days of the

date of this notice, you must do one of the following:  1) Correct the violations, 2)Apply for

the permits associated the case of work requiring a permit, an application for permit shall

be submitted.   A re-inspection of the premises will occur on 2/11/2008  at which time

compliance will be required.  If you decide to withdraw the application for legalization, the

inspection will verify that the unit(s) have been removed.   Failure to comply will result in

this office referring the matter to the City of Portland Corporation Counsel for legal action

and possible civil penalties, as provided for in Section 6-1 of the Code.

This constitutes an appealable decision pursuant to Section 6-127 of the Code.

Please feel free to contact me if you wish to discuss the matter or have any questions.

Please be advised that the Portland City Council has amended the Building regulations to

Include a $75.00 re-inspection fee. This violation will automatically cause a re-inspection at

No charge. If there are any subsequent inspections, however, the $75.00 fee will be assessed

For each inspection, unless it is associated with an approved permit.

Sincerely,

Suzanne Hunt @ (207) 874-8707

Building Inspector