04P156

TO:       	Ethan Boxer Macomber – Planner

FROM:  	Jim Seymour – Development Review Coordinator, Sebago Technics, Inc.

# RE:       	Chabad Lubavitch of Maine, Pomeroy Street: Synagogue & Family Home

DATE:   	January 14, 2005

Sebago Technics has reviewed the revised Site Plan and supporting documentation for the proposed Synagogue and family home to be located off Pomeroy Street.  The following comments are submitted in outline format:

1.	Stormwater Management

A.	Care must be taken not to direct any additional stormwater runoff onto adjacent properties located along Bancroft Street as a result of the proposed project being constructed.  Upon a site walk, it was apparent much off-site runoff crosses the property, and the site soil conditions are of very poor fine sand and silt.

B.	The design of the proposed Pomeroy Street must conform to City standards for all utilities including drainage. We are concerned with the connections of the storm drain into the apparent combined sewer of Bancroft Street.  Currently there appears to be much surface flows that get conveyed by sinkholes or unidentified channels underground. Given displacement of mapped wetlands it is clear that the road will need under drains and catch basin with curb line design for stormwater collection. All catch basin connections shall be done to a drain manhole, in accordance to City required locations within the street and constructed per the City specifications.

C.	Due to the requirement to construct the entire street of Pomeroy Street, the street section shall be curbed both sides, with a drain main line extending to the intersection of Motley Street and then ditch culverts as designed shall be completed to collect offsite runoff now, and be converted to a main in the future if Motley St. were to be developed.

D.	The engineer shall review the spillway design, which could overflow the front yard and verify the potential impacts in events over 25 year (prefer 100 yr storm) to check flood elevations or street impacts from flooding condition.

E.	All drainage and sewer structures located on the plan and profile sheet section, and pipes to be in the right-of way of Pomeroy Street shall be indicated on the plans with the design inverts from pipe connections, and pipe lengths and slopes.

F.	Typical stage storage elevations for the design storm flood elevations along with a construction detail of the ponds are needed.

G.	Please verify that runoff from the adjacent Redlon St. Development does or does not impact this project with surface runoff. Some perceptions of abutters are that the Redlon Street project does currently sheds runoff to their properties. Evidence to the actual drainage pattern will be appreciated and worth the effort to add proof and comfort to the abutters served by this project, as you could be perceived to further aggravate their impacts, with which the have expressed concerns.

2.	Road Access/Circulation

The section of street for Pomeroy Street shall be built to City design standards for sewer, storm drain, and all utilities, which must be in the locations as specified within City Standards for the entire street.  The typical street cross section shall be placed on the recording plat.

The applicant shall obtain current information regarding the existing utilities, and manholes in Bancroft Street to determine whether there is adequate capacity for additional sewer and/or storm flows from Public Works. Also construction notes are needed (I e. Dig Safe notice, Street permits required, Pre-application meetings, etc).

Parking Lot Issues

- Snow storage location to be identified

- Handicapped access and spaces shown

- Curbing or wheel stops shown along sidewalk to building.

Street Issues

- Recommend more catch basins; the length of flow is too long along curb line.

- The streets shall have the proper stop signs and pavement markings for traffic      controls.

- Streetlights are required at intersections.

- Sidewalk waiver will be needed to eliminate one side of sidewalk on Pomeroy Street.

- Underdrains will be required due to poor sub-soils and saturation.

- Recommend 8-inch water and sewer main for future connectivity.  Please obtain input from the Portland Water District to provide recommendations for potential future growth and development expansion off of Pomeroy or Motley Streets for Water services. Sewer shall be extended to at least the intersection with Kenilworth Street.

3.	Grading/Erosion Control

A.	Provide inlet protection with silt sacs for catch basins in Pomeroy and Bancroft Street.

B.	Appropriate BMPs are shown installed on the plan, however we recommend a double barrier along residential properties.

C.	Although the contour grades are shown, the plan will be more beneficial if spot elevations can be provided along the building and parking lot as well.  Spot grades are useful if the ones shown represent finish grades in areas where drainage is of concern or elevation is critical in relation to the existing or proposed structure. Please indicate top of foundation grades and finish garage grades on the plans for reference.

4.	Utility Installation/Location

- Letters must be obtained from utilities stating that adequate capacity exists.

- Please show where underground electrical utility services will be installed.

- Please indicate where a new hydrant will be located if required by the fire department and the current closest hydrant to the property with travel distance to the proposed structure.

5.	General

A.	Some trees are shown planted for a visual buffer, along with other street trees as required to meet City specifications. Please refer to comments from the City Arborist regarding landscaping requirements.

- As a result of the development of the property, does the parcel have adequate area for snow storage?  The snow storage areas should be designated on the plan.  The concern is with how snow melts in areas apparently available for snow storage will affect neighboring properties.

- Will blasting of ledge be required to install the building foundations or utility trenches? Please add notes regarding if ledge removal will be conducted and if it is describe the manner that it will be performed. We request the information based on an adjacent development requiring much blasting.

D. 	Please clearly delineate wetland limits, anticipated filling areas, permits to be acquired, along with the wetland specialist whom performed the identification.

6.	Details

A.	Need to provide typical details for the following: driveway/parking lot pavement buildup section with dimensions and materials, underdrain, and granite curb.

- Appropriate BMP details shall be included on the detail plan sheet.

It is our understanding that there is another development that would require the use of Pomeroy Street to develop a section of Kenilworth Street for a residential subdivision. We have requested that the City and the applicants work together to coordinate a shared process and costs for constructing Pomeroy Street.  The applicants engineering firm represents both applicants and may be able to assist in the combining of efforts to share costs and coordination. Please contact our office with any questions.

JRS:jrs