## 23 July 2007

Mr. William A. Thompson,

Project Manager,

Berry, Huff, McDonald, and Milligan, Inc.,

28 State Street,

Gorham, Maine 04038

# RE: The Capacity to Handle Wastewater Flows, from the Proposed Residence

# and Assembly Area, for Chabad Lubobitch, at 123 Pomeroy Street.

Dear Mr. Thompson:

The existing eighteen-inch diameter vitrified clay sewer pipe located in Bancroft Street has adequate capacity to transport, while The Portland Water District sewage treatment facilities, located off Marginal Way, have adequate capacity to treat the total increase in wastewater flows of 1,044 GPD, from the proposed building project.

Anticipated Wastewater Flows from the Proposed Building Project:

9 Proposed Bedrooms @ 90 GPD/Bedroom				=    990 GPD

27 Proposed Fixed Assembly Seats @ 2 GPD/Fixed Seat			=      54 GPD

Total Proposed Increase in Wastewater Flows for this Project 		= 1,044 GPD

The City combined sewer overflow (C.S.O.) abatement consent agreement (with the U.S.E.P.A., and with the Maine D.E.P.) requires C.S.O. abatement, as well as storm water mitigation, in order to offset any increase in sanitary flows, from all projects.  If the City can be of further assistance, please call 874-8832.

Sincerely,

CITY OF PORTLAND

Frank J Brancely, B.A., M.A.

Senior Engineering Technician

FJB

cc:	Alexander Q. Jaegerman, Director, Planning Division, Department of Planning, and Urban Development, City of Portland

Barbara Barhydt, Development Review Services Manager, Department of Planning, and Urban Development, City of Portland

Penny Littell, Associate Corporation Counsel, Corporation Counsel, City of Portland

Michael Farmer, P.E., Project Engineer, City of Portland

Bradley A. Roland, P.E., Environmental Projects Engineer, City of Portland

Stephen K. Harris, Assistant Engineer, City of Portland

Jane Ward, Administrative Assistant, City of Portland

William A. Thompson, Project Manager, Berry, Huff, McDonald, and Milligan, Incorporated.

Desk file