Copyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 092900 - GYPSUM BOARD

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

      - SUMMARY

        - This Section includes the following:

Adjust list below to suit Project.

          - Interior gypsum board.

        - Related Sections include the following:

List below only products and construction that the reader might expect to find in this Section but are specified elsewhere.

          - Division 9 Section "Non-Structural Metal Framing" for non-structural framing and suspension systems that support gypsum board.

          - Division 9 Painting Section for primers applied to gypsum board surfaces.

      - SUBMITTALS

        - Product Data:  For each type of product indicated.

      - QUALITY ASSURANCE

Retain paragraph below where gypsum board is part of fire-resistance-rated assemblies.  Indicate design designations of specific assemblies on Drawings.

Retain paragraph below where gypsum board is part of STC-rated assemblies.  Indicate design designations of specific assemblies on Drawings.

        - STC-Rated Assemblies:  For STC-rated assemblies, provide materials and construction identical to those tested in assembly indicated according to ASTM E 90 and classified according to ASTM E 413 by an independent testing agency.

      - STORAGE AND HANDLING

        - Store materials inside under cover and keep them dry and protected against damage from weather, condensation, direct sunlight, construction traffic, and other causes.  Stack panels flat to prevent sagging.

      - PROJECT CONDITIONS

        - Environmental Limitations:  Comply with ASTM C 840 requirements or gypsum board manufacturer's written recommendations, whichever are more stringent.

Delete first paragraph below if infeasible for fast-track construction.

        - Do not install interior products until installation areas are enclosed and conditioned.

        - Do not install panels that are wet, those that are moisture damaged, and those that are mold damaged.

          - Indications that panels are wet or moisture damaged include, but are not limited to, discoloration, sagging, or irregular shape.

          - Indications that panels are mold damaged include, but are not limited to, fuzzy or splotchy surface contamination and discoloration.

- PRODUCTS

      - PANELS, GENERAL

Retain first paragraph below to specify recycled content if required for LEED-NC or LEED-CI Credits MR 4.1 and MR 4.2.  Recycled content of gypsum board varies greatly; consult manufacturers before inserting requirement.  An alternative method of meeting LEED Credit MR 4.1 and MR 4.2 requirements is to retain requirement in Division 1 Section "LEED Requirements" that gives Contractor option and responsibility for determining how LEED Credit MR 4.1 and MR 4.2 requirement will be met.

        - Recycled Content:  Provide gypsum panel products with recycled content such that postconsumer recycled content plus one-half of preconsumer recycled content constitutes a minimum of 25 percent by weight.

        - Size:  Provide in maximum lengths and widths available that will minimize joints in each area and that correspond with support system indicated.

      - INTERIOR GYPSUM BOARD

ASTM C 36/C 36M is traditional standard used to specify regular and Type X gypsum board; ASTM C 1396/C 1396M includes regular, Type X, ceiling, and exterior-soffit gypsum board, as well as other types of gypsum board panels.  Both standards are listed below to avoid confusion because manufacturers may only list compliance with one standard when compliance with either is satisfactory.

        - General:  Complying with ASTM C 36/C 36M or ASTM C 1396/C 1396M, as applicable to type of gypsum board indicated and whichever is more stringent.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 1 Section "Product Requirements."

          - Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

          - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

            - American Gypsum Co.

            - BPB America Inc.

G-P Gypsum offers two different product lines, one that is paper faced on both sides ("ToughRock") and one that incorporates patented embedded glass mats on concealed surfaces ("DensArmor").  If products with embedded glass mats are required, revise the Section Text accordingly.

            - G-P Gypsum.

            - Lafarge North America Inc.

            - National Gypsum Company.

            - PABCO Gypsum.

            - Temple.

            - USG Corporation.

        - Regular Type:

Regular-type gypsum panels are also available in 1/4- and 3/8-inch (6.4- and 9.5-mm) thicknesses for limited applications.

          - Thickness:  5/8 inch (12.7 mm).

          - Long Edges:  Tapered.

        - Type X (Special Fire-Resistant)

          - Thickness: 5/8 inch

          - Long Edges: tapered.

Type C gypsum board has fire-resistive capability greater than that of Type X.  For rated assemblies, panels from different manufacturers cannot be intermixed because ratings apply only to assemblies identical in materials and construction to those tested.  Design designations of independent testing agencies indicated on Drawings generally determine product requirements for Type C gypsum board.

      - TRIM ACCESSORIES

        - Interior Trim:  ASTM C 1047.

          - Material:  Galvanized or aluminum-coated steel sheet, rolled zinc, plastic, or paper-faced galvanized steel sheet.

          - Shapes:

            - Cornerbead.

            - Bullnose bead.

            - LC-Bead:  J-shaped; exposed long flange receives joint compound.

            - L-Bead:  L-shaped; exposed long flange receives joint compound.

            - U-Bead:  J-shaped; exposed short flange does not receive joint compound.

            - Expansion (control) joint.

            - Curved-Edge Cornerbead:  With notched or flexible flanges.

Show dimensions and profiles of aluminum trim on Drawings.

      - JOINT TREATMENT MATERIALS

        - General:  Comply with ASTM C 475/C 475M.

        - Joint Tape:

          - Interior Gypsum Wallboard:  Paper.

        - Joint Compound for Interior Gypsum Wallboard:  For each coat use formulation that is compatible with other compounds applied on previous or for successive coats.

See "Joint Compound" Article in the Evaluations.

          - Prefilling:  At open joints, rounded or beveled panel edges, and damaged surface areas, use setting-type taping compound.

          - Embedding and First Coat:  For embedding tape and first coat on joints, fasteners, and trim flanges, use drying-type, all-purpose compound.

            - Use setting-type compound for installing paper-faced metal trim accessories.

          - Fill Coat:  For second coat, use drying-type, all-purpose compound.

          - Finish Coat:  For third coat, use setting-type, sandable topping compound.

          - Skim Coat:  For final coat of Level 5 finish, use setting-type, sandable topping compound.

      - AUXILIARY MATERIALS

        - General:  Provide auxiliary materials that comply with referenced installation standards and manufacturer's written recommendations.

        - Steel Drill Screws:  ASTM C 1002, unless otherwise indicated.

Delete subparagraph below if panels are not attached to cold-formed metal framing specified in Division 5.

          - Use screws complying with ASTM C 954 for fastening panels to steel members from 0.033 to 0.112 inch (0.84 to 2.84 mm) thick.

Delete subparagraph below if no cementitious backer units.

        - Sound Attenuation Blankets:  ASTM C 665, Type I (blankets without membrane facing) produced by combining thermosetting resins with mineral fibers manufactured from glass, slag wool, or rock wool.

Retain subparagraph below to specify recycled content if required for LEED-NC or LEED-CI Credits MR 4.1 and MR 4.2.  An alternative method of meeting LEED Credit MR 4.1 and MR 4.2 requirements is to retain requirement in Division 1 Section "LEED Requirements" that gives Contractor option and responsibility for determining how LEED Credit MR 4.1 and MR 4.2 requirement will be met.

          - Recycled Content:  Provide blankets with recycled content such that postconsumer recycled content plus one-half of preconsumer recycled content constitutes a minimum of 25 percent by weight.

        - Acoustical Sealant:  As specified in Division 7 Section "Joint Sealants."

Retain subparagraph below if low-emitting materials are required for LEED-NC or LEED-CI Credit EQ 4.1.  VOC limit is that for architectural sealants.

          - Provide sealants that have a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

- EXECUTION

      - EXAMINATION

        - Examine areas and substrates, with Installer present, and including welded hollow-metal frames and framing, for compliance with requirements and other conditions affecting performance.

        - Examine panels before installation.  Reject panels that are wet, moisture damaged, and mold damaged.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - APPLYING AND FINISHING PANELS, GENERAL

        - Comply with ASTM C 840.

        - Install ceiling panels across framing to minimize the number of abutting end joints and to avoid abutting end joints in central area of each ceiling.  Stagger abutting end joints of adjacent panels not less than one framing member.

        - Install panels with face side out.  Butt panels together for a light contact at edges and ends with not more than 1/16 inch (1.5 mm) of open space between panels.  Do not force into place.

        - Locate edge and end joints over supports, except in ceiling applications where intermediate supports or gypsum board back-blocking is provided behind end joints.  Do not place tapered edges against cut edges or ends.  Stagger vertical joints on opposite sides of partitions.  Do not make joints other than control joints at corners of framed openings.

        - Form control and expansion joints with space between edges of adjoining gypsum panels.

        - Cover both faces of support framing with gypsum panels in concealed spaces (above ceilings, etc.), except in chases braced internally.

          - Unless concealed application is indicated or required for sound, fire, air, or smoke ratings, coverage may be accomplished with scraps of not less than 8 sq. ft. (0.7 sq. m) in area.

          - Fit gypsum panels around ducts, pipes, and conduits.

          - Where partitions intersect structural members projecting below underside of floor/roof slabs and decks, cut gypsum panels to fit profile formed by structural members; allow 1/4- to 3/8-inch- (6.4- to 9.5-mm-) wide joints to install sealant.

Detail perimeter isolation on Drawings.  See "Crack Control" Article in the Evaluations.

        - Isolate perimeter of gypsum board applied to non-load-bearing partitions at structural abutments, except floors.  Provide 1/4- to 1/2-inch- (6.4- to 12.7-mm-) wide spaces at these locations, and trim edges with edge trim where edges of panels are exposed.  Seal joints between edges and abutting structural surfaces with acoustical sealant.

        - Attachment to Steel Framing:  Attach panels so leading edge or end of each panel is attached to open (unsupported) edges of stud flanges first.

Retain paragraph below for wood framing where fire ratings are not required.

        - STC-Rated Assemblies:  Seal construction at perimeters, behind control joints, and at openings and penetrations with a continuous bead of acoustical sealant.  Install acoustical sealant at both faces of partitions at perimeters and through penetrations.  Comply with ASTM C 919 and with manufacturer's written recommendations for locating edge trim and closing off sound-flanking paths around or through assemblies, including sealing partitions above acoustical ceilings.

        - Install sound attenuation blankets before installing gypsum panels, unless blankets are readily installed after panels have been installed on one side.

      - APPLYING INTERIOR GYPSUM BOARD

        - Install interior gypsum board in the following locations:

          - Regular Type:  Vertical surfaces, unless otherwise indicated.

        - Single-Layer Application:

Delete first subparagraph below if no gypsum board ceilings.

          - On partitions/walls, apply gypsum panels horizontally (perpendicular to framing), unless otherwise indicated or required by fire-resistance-rated assembly, and minimize end joints.

            - Stagger abutting end joints not less than one framing member in alternate courses of panels.

Usually retain first subparagraph below if vertical application of panels is specified.

          - Fastening Methods:  Apply gypsum panels to supports with steel drill screws.

      - FIRE-RESISTANT ASSEMBLIES

        - Wherever fire-rated construction is indicated, provide materials and application methods, including types and spacing of fasteners, wall and ceiling framing in accordance with the specifications contained in UL Fire Resistance for the Design Number(s) indicated, or GA 600 for the File Number(s) indicated. Joints of fire-rated gypsum board enclosures shall be closed and sealed in accordance with UL test requirements or GA requirements. Seal penetrations through rated partitions and ceilings tight in accordance with tested systems.

      - INSTALLING TRIM ACCESSORIES

        - General:  For trim with back flanges intended for fasteners, attach to framing with same fasteners used for panels.  Otherwise, attach trim according to manufacturer's written instructions.

Generally, retain first option in first paragraph below and show joints on Drawings.  See "Crack Control" Article in the Evaluations for discussion of control joints.

        - Control Joints:  Install control joints according to ASTM C 840 and in specific locations approved by Contracting Officer for visual effect.

        - Interior Trim:  Install in the following locations:

          - Cornerbead:  Use at outside corners.

          - LC-Bead:  Use at exposed panel edges.

          - Curved-Edge Cornerbead:  Use at curved openings.

      - FINISHING GYPSUM BOARD

        - General:  Treat gypsum board joints, interior angles, edge trim, control joints, penetrations, fastener heads, surface defects, and elsewhere as required to prepare gypsum board surfaces for decoration.  Promptly remove residual joint compound from adjacent surfaces.

        - Prefill open joints, rounded or beveled edges, and damaged surface areas.

        - Apply joint tape over gypsum board joints, except those with trim having flanges not intended for tape.

See "Gypsum Board Finish Levels" Article in the Evaluations for a discussion of requirements of various levels.

        - Gypsum Board Finish Levels:  Finish panels to levels indicated below and according to ASTM C 840:

Gypsum board finish levels are minimum requirements established by ASTM C 840 without elaboration.  Edit or modify the following subparagraphs based on project conditions.

Level 4 is suitable for surfaces receiving light-textured finishes, wallcoverings, and flat paints.  It is generally the standard exposed finish.  Gloss and semi-gloss enamel paints are not usually recommended over this level of finish.  ASTM C 840 requires application of "drywall primer" on surfaces before final decoration.  Specify priming of gypsum board surfaces in Division 9 painting Sections.

          - Level 4:  At panel surfaces that will be exposed to view, unless otherwise indicated.

            - Primer and its application to surfaces are specified in other Division 9 Sections.

      - PROTECTION

        - Protect installed products from damage from weather, condensation, direct sunlight, construction, and other causes during remainder of the construction period.

        - Remove and replace panels that are wet, moisture damaged, and mold damaged.

          - Indications that panels are wet or moisture damaged include, but are not limited to, discoloration, sagging, or irregular shape.

          - Indications that panels are mold damaged include, but are not limited to, fuzzy or splotchy surface contamination and discoloration.

END OF SECTION 092900