Copyright 2008 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 220719 - PLUMBING PIPING INSULATION

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section includes insulating the following plumbing piping services:

The list of plumbing piping below matches the various piping systems in the schedule articles.  Coordinate the revision of list below with "Piping Insulation Schedule, General," "Indoor Piping Insulation Schedule," "Outdoor, Aboveground Piping Insulation Schedule," and "Outdoor, Underground Piping Insulation Schedule" articles.

          - Domestic cold-water piping.

          - Domestic hot-water piping.

          - Sanitary waste piping exposed to ceiling plenums.

          - Supplies and drains for handicap-accessible lavatories and sinks.

        - Related Sections:

Retain Section in subparagraph below that contains requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Division 22 Section "Plumbing Equipment Insulation."

      - SUBMITTALS

First four paragraphs below are defined in Division 01 Section "Submittal Procedures" as "action submittals."

        - Product Data:  For each type of product indicated.  Include thermal conductivity, water-vapor permeance thickness, and jackets (both factory- and field-applied, if any).

      - QUALITY ASSURANCE

Retain first paragraph below if available at Project location.  Apprenticeship programs are usually associated with union shops.  Other craft training programs are available.

        - Installer Qualifications:  Skilled mechanics who have successfully completed an apprenticeship program or another craft training program certified by the Department of Labor, Bureau of Apprenticeship and Training.

When fire-performance characteristics are important requirements, verify surface-burning characteristics of insulation materials by an independent testing agency and require test report submittals.

        - Surface-Burning Characteristics:  For insulation and related materials, as determined by testing identical products according to ASTM E 84 by a testing agency acceptable to authorities having jurisdiction.  Factory label insulation and jacket materials and adhesive, mastic, tapes, and cement material containers, with appropriate markings of applicable testing agency.

          - Insulation Installed Indoors:  Flame-spread index of 25 or less, and smoke-developed index of 50 or less.

          - Insulation Installed Outdoors:  Flame-spread index of 75 or less, and smoke-developed index of 150 or less.

If retaining "Mockups" Paragraph below, indicate location, size, and other details of mockups on Drawings or by inserts.  Revise if only one mockup is required.

        - Comply with the following applicable standards and other requirements specified for miscellaneous components:

          - Supply and Drain Protective Shielding Guards:  ICC A117.1.

      - DELIVERY, STORAGE, AND HANDLING

Retain this article to require shipping container markings.  Container marking is an option in ASTM standards; default condition does not include the marking in this article unless specified in the Contract.

        - Packaging:  Insulation material containers shall be marked by manufacturer with appropriate ASTM standard designation, type and grade, and maximum use temperature.

      - COORDINATION

        - Coordinate sizes and locations of supports, hangers, and insulation shields specified in Division 22 Section "Hangers and Supports for Plumbing Piping and Equipment."

        - Coordinate clearance requirements with piping Installer for piping insulation application.  Before preparing piping Shop Drawings, establish and maintain clearance requirements for installation of insulation and field-applied jackets and finishes and for space required for maintenance.

        - Coordinate installation and testing of heat tracing.

      - SCHEDULING

        - Schedule insulation application after pressure testing systems and, where required, after installing and testing heat tracing.  Insulation application may begin on segments that have satisfactory test results.

        - Complete installation and concealment of plastic materials as rapidly as possible in each area of construction.

- PRODUCTS

      - INSULATION MATERIALS

If retaining more than one type of insulation in this article, indicate where each type applies in insulation system schedules.

        - Comply with requirements in "Piping Insulation Schedule, General," and "Indoor Piping Insulation Schedule," articles for where insulating materials shall be applied.

See "Product Characteristics" Article in Evaluations for comparisons and temperature ranges for insulation material properties.

        - Products shall not contain asbestos, lead, mercury, or mercury compounds.

        - Products that come in contact with stainless steel shall have a leachable chloride content of less than 50 ppm when tested according to ASTM C 871.

        - Insulation materials for use on austenitic stainless steel shall be qualified as acceptable according to ASTM C 795.

        - Foam insulation materials shall not use CFC or HCFC blowing agents in the manufacturing process.

        - Cellular Glass:  Inorganic, incombustible, foamed or cellulated glass with annealed, rigid, hermetically sealed cells.  Factory-applied jacket requirements are specified in "Factory-Applied Jackets" Article.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

            - Pittsburgh Corning Corporation; Foamglas.

            - Approved equal.

          - Block Insulation:  ASTM C 552, Type I.

          - Special-Shaped Insulation:  ASTM C 552, Type III.

If retaining both types of insulation in first two subparagraphs below, indicate where each type applies in insulation system schedules.

          - Preformed Pipe Insulation without Jacket:  Comply with ASTM C 552, Type II, Class 1.

          - Preformed Pipe Insulation with Factory-Applied [ASJ] [ASJ-SSL]:  Comply with ASTM C 552, Type II, Class 2.

          - Factory fabricate shapes according to ASTM C 450 and ASTM C 585.

"Flexible Elastomeric Insulation" Paragraph below is unsuitable for temperatures lower than minus 70 deg F (minus 57 deg C) and higher than 220 deg F (104 deg C).

        - Mineral-Fiber, Preformed Pipe Insulation:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

            - Fibrex Insulations Inc.; Coreplus 1200.

            - Johns Manville; Micro-Lok.

            - Knauf Insulation; 1000-Degree Pipe Insulation.

            - Manson Insulation Inc.; Alley-K.

            - Owens Corning; Fiberglas Pipe Insulation.

            - Approved equal.

ASJ requires field-applied adhesive and staples.  ASJ-SSL does not require field-applied adhesive and staples, resulting in reduced installation labor.

          - Type I, 850 Deg F (454 Deg C) Materials:  Mineral or glass fibers bonded with a thermosetting resin.  Comply with ASTM C 547, Type I, Grade A, with factory-applied ASJ.  Factory-applied jacket requirements are specified in "Factory-Applied Jackets" Article.

Phenolic insulation is available in Grades 1 and 2.  Grade 1 has a lower thermal conductivity than Grade 2.  Grade 2 is not commercially available.

      - INSULATING CEMENTS

Mineral-fiber insulating cement is suitable for temperatures from 100 to 1600 deg F (38 to 871 deg C).  Vermiculite insulating cement is suitable for temperatures from 100 to 1800 deg F (38 to 982 deg C).

        - Mineral-Fiber Insulating Cement:  Comply with ASTM C 195.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

            - Ramco Insulation, Inc.; Super-Stik.

            - Approved equal.

Mineral-fiber, hydraulic-setting cement is suitable for temperatures from 100 to 1200 deg F (38 to 649 deg C) and for a smooth surface.

        - Mineral-Fiber, Hydraulic-Setting Insulating and Finishing Cement:  Comply with ASTM C 449.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements available products that may be incorporated into the Work include, but are not limited to, the following:

            - Ramco Insulation, Inc.; Ramcote 1200 and Quik-Cote.

            - Approved equal.

      - ADHESIVES

Military Specification in this article was the only standard available when this Section was written.  MIL-A-3316C was last updated in October 1987.

        - Materials shall be compatible with insulation materials, jackets, and substrates and for bonding insulation to itself and to surfaces to be insulated, unless otherwise indicated.

Product attributes in first paragraph below are based on Foster Brand products; there are variations among manufacturers.

        - Cellular-Glass Adhesive:  Two-component, thermosetting urethane adhesive containing no flammable solvents, with a service temperature range of minus 100 to plus 200 deg F (minus 73 to plus 93 deg C).

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

            - Foster Brand, Specialty Construction Brands, Inc., a business of H. B. Fuller Company; 81-84.

            - Approved equal.

Retain first subparagraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit EQ 4.1.

          - For indoor applications, use adhesive that has a VOC content of 50 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Subparagraph below applies to LEED for Schools.

          - Use adhesive that complies with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers," including 2004 Addenda.

        - Mineral-Fiber Adhesive:  Comply with MIL-A-3316C, Class 2, Grade A.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

            - Childers Brand, Specialty Construction Brands, Inc., a business of H. B. Fuller Company; CP-127.

            - Eagle Bridges - Marathon Industries; 225.

            - Foster Brand, Specialty Construction Brands, Inc., a business of H. B. Fuller Company; 85-60/85-70.

            - Mon-Eco Industries, Inc.; 22-25.

            - Approved equal.

Retain first subparagraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit EQ 4.1.

          - For indoor applications, use adhesive that has a VOC content of 80 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Subparagraph below applies to LEED for Schools.

          - Use adhesive that complies with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers," including 2004 Addenda.

        - ASJ Adhesive, and FSK Jacket Adhesive:  Comply with MIL-A-3316C, Class 2, Grade A for bonding insulation jacket lap seams and joints.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

            - Childers Brand, Specialty Construction Brands, Inc., a business of H. B. Fuller Company; CP-82.

            - Eagle Bridges - Marathon Industries; 225.

            - Foster Brand, Specialty Construction Brands, Inc., a business of H. B. Fuller Company; 85-20.

            - Mon-Eco Industries, Inc.; 22-25.

            - Approved equal.

Retain first subparagraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit EQ 4.1.

          - For indoor applications, use adhesive that has a VOC content of 50 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Subparagraph below applies to LEED for Schools.

          - Use adhesive that complies with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers," including 2004 Addenda.

        - PVC Jacket Adhesive:  Compatible with PVC jacket.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

            - Dow Corning Corporation; 739, Dow Silicone.

            - Johns Manville; Zeston Perma-Weld, CEEL-TITE Solvent Welding Adhesive.

            - P.I.C. Plastics, Inc.; Welding Adhesive.

            - Speedline Corporation; Polyco VP Adhesive.

            - Approved equal.

Retain first subparagraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit EQ 4.1.

          - For indoor applications, use adhesive that has a VOC content of 50 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Subparagraph below applies to LEED for Schools.

          - Use adhesive that complies with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers," including 2004 Addenda.

      - MASTICS

The industry does not have a clear definition that categorizes mastics into vapor barriers, vapor retarders, and breather mastics.  Specification follows the nomenclature used by Foster.  Products with a perm rating of 0.1 and lower are considered vapor barriers.  Products with a perm rating greater than 0.1 and less than 1.0 are considered vapor retarders.  Products with a perm rating greater than 1.0 are called "breathable."  Consider ambient conditions and operating temperatures when selecting a mastic.  Consider using water-based mastics for environmental reasons.

LEED Credit EQ 4.1 does not address requirements for mastics.

        - Materials shall be compatible with insulation materials, jackets, and substrates; comply with MIL-PRF-19565C, Type II.

Retain subparagraph below if low-emitting materials are required.  Consult mastic manufacturers to determine VOC limits.

          - For indoor applications, use mastics that have a VOC content of 50 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Verify that products listed comply with water-vapor permeance.  Require proof of performance and certified test reports from vapor-barrier mastic manufacturer to support product literature claims.

Retain one of four mastic paragraphs below.  Product attributes in first paragraph are based on Foster; there are variations among manufacturers.

        - Vapor-Barrier Mastic:  Water based; suitable for indoor use on below-ambient services.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

            - Foster Brand, Specialty Construction Brands, Inc., a business of H. B. Fuller Company; 30-80/30-90.

            - Vimasco Corporation; 749.

            - Approved equal.

          - Water-Vapor Permeance:  ASTM E 96/E 96M, Procedure B, 0.013 perm (0.009 metric perm) at 43-mil (1.09-mm) dry film thickness.

          - Service Temperature Range:  Minus 20 to plus 180 deg F (Minus 29 to plus 82 deg C).

          - Solids Content:  ASTM D 1644, 58 percent by volume and 70 percent by weight.

          - Color:  White.

        - Breather Mastic:  Water based; suitable for indoor and outdoor use on above-ambient services.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

            - Childers Brand, Specialty Construction Brands, Inc., a business of H. B. Fuller Company; CP-10.

            - Eagle Bridges - Marathon Industries; 550.

            - Foster Brand, Specialty Construction Brands, Inc., a business of H. B. Fuller Company; 46-50.

            - Mon-Eco Industries, Inc.; 55-50.

            - Vimasco Corporation; WC-1/WC-5.

            - Approved equal.

          - Water-Vapor Permeance:  ASTM F 1249, 1.8 perms (1.2 metric perms) at 0.0625-inch (1.6-mm) dry film thickness.

          - Service Temperature Range:  Minus 20 to plus 180 deg F (Minus 29 to plus 82 deg C).

          - Solids Content:  60 percent by volume and 66 percent by weight.

          - Color:  White.

      - LAGGING ADHESIVES

LEED Credit EQ 4.1 does not address requirements for lagging adhesives.

        - Description:  Comply with MIL-A-3316C, Class I, Grade A, and shall be compatible with insulation materials, jackets, and substrates.

Retain first subparagraph below if low-emitting materials are required.  Consult lagging adhesive manufacturers to determine VOC limits.

          - For indoor applications, use lagging adhesives that have a VOC content of 50 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements available products that may be incorporated into the Work include, but are not limited to, the following ]:

            - Childers Brand, Specialty Construction Brands, Inc., a business of H. B. Fuller Company; CP-50 AHV2.

            - Foster Brand, Specialty Construction Brands, Inc., a business of H. B. Fuller Company; 30-36.

            - Vimasco Corporation; 713 and 714.

            - Approved equal.

          - Fire-resistant, water-based lagging adhesive and coating for use indoors to adhere fire-resistant lagging cloths over pipe insulation.

          - Service Temperature Range:  0 to plus 180 deg F (Minus 18 to plus 82 deg C).

          - Color:  White.

      - SEALANTS

Sealants are categorized into "joint sealants" and "flashing sealants."  Joint sealants are primarily used for vapor sealing longitudinal seams and butt joints of insulation materials.  Flashing sealants are primarily used for sealing jacket and mastic materials.

        - Joint Sealants:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Joint Sealants for Cellular-Glass and Phenolic Products:  Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

            - Childers Brand, Specialty Construction Brands, Inc., a business of H. B. Fuller Company; CP-76.

            - Eagle Bridges - Marathon Industries; 405.

            - Foster Brand, Specialty Construction Brands, Inc., a business of H. B. Fuller Company; 30-45.

            - Mon-Eco Industries, Inc.; 44-05.

            - Pittsburgh Corning Corporation; Pittseal 444.

            - Approved equal.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Materials shall be compatible with insulation materials, jackets, and substrates.

          - Permanently flexible, elastomeric sealant.

          - Service Temperature Range:  Minus 100 to plus 300 deg F (Minus 73 to plus 149 deg C).

          - Color:  White or gray.

Retain first subparagraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit EQ 4.1.

          - For indoor applications, use sealants that have a VOC content of 420 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Subparagraph below applies to LEED for Schools.

          - Use sealants that comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers," including 2004 Addenda.

Materials in first paragraph below are for sealing metal jacket seams and joints.

        - FSK and Metal Jacket Flashing Sealants:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, the following:

            - Childers Brand, Specialty Construction Brands, Inc., a business of H. B. Fuller Company; CP-76.

            - Eagle Bridges - Marathon Industries; 405.

            - Foster Brand, Specialty Construction Brands, Inc., a business of H. B. Fuller Company; 95-44.

            - Mon-Eco Industries, Inc.; 44-05.

            - Approved equal.

          - Materials shall be compatible with insulation materials, jackets, and substrates.

          - Fire- and water-resistant, flexible, elastomeric sealant.

          - Service Temperature Range:  Minus 40 to plus 250 deg F (Minus 40 to plus 121 deg C).

          - Color:  Aluminum.

Retain first subparagraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit EQ 4.1.

          - For indoor applications, use sealants that have a VOC content of 420 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Subparagraph below applies to LEED for Schools.

          - Use sealants that comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers," including 2004 Addenda.

        - ASJ Flashing Sealants, and Vinyl, PVDC, and PVC Jacket Flashing Sealants:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

            - Childers Brand, Specialty Construction Brands, Inc., a business of H. B. Fuller Company; CP-76.

            - Approved equal.

          - Materials shall be compatible with insulation materials, jackets, and substrates.

          - Fire- and water-resistant, flexible, elastomeric sealant.

          - Service Temperature Range:  Minus 40 to plus 250 deg F (Minus 40 to plus 121 deg C).

          - Color:  White.

Retain first subparagraph below if required for LEED-NC, LEED-CI, or LEED-CS Credit EQ 4.1.

          - For indoor applications, use sealants that have a VOC content of 420 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Subparagraph below applies to LEED for Schools.

          - Use sealants that comply with the testing and product requirements of the California Department of Health Services' "Standard Practice for the Testing of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers," including 2004 Addenda.

      - FACTORY-APPLIED JACKETS

Coordinate types of factory-applied jacket insulation materials selected and types of factory-applied jackets indicated in insulation system schedules.

For insulation materials with factory-applied jackets for use on applications above 140 deg F (60 deg C), specify sufficient insulation thickness to maintain outer surface temperature of insulation below 140 deg F (60 deg C).  140 deg F (60 deg C) surface temperature is set by OSHA for personnel protection.

        - Insulation system schedules indicate factory-applied jackets on various applications.  When factory-applied jackets are indicated, comply with the following:

          - ASJ:  White, kraft-paper, fiberglass-reinforced scrim with aluminum-foil backing; complying with ASTM C 1136, Type I.

          - ASJ-SSL:  ASJ with self-sealing, pressure-sensitive, acrylic-based adhesive covered by a removable protective strip; complying with ASTM C 1136, Type I.

          - FSK Jacket:  Aluminum-foil, fiberglass-reinforced scrim with kraft-paper backing; complying with ASTM C 1136, Type II.

      - FIELD-APPLIED FABRIC-REINFORCING MESH

Both glass-fiber- and polyester-fabric-reinforcing meshes are acceptable.

Retain two paragraphs below to give Contractor option to use either glass-fiber or polyester fabric.

        - Woven Glass-Fiber Fabric:  Approximately 2 oz./sq. yd. (68 g/sq. m) with a thread count of 10 strands by 10 strands/sq. in. (4 strands by 4 strands/sq. mm) for covering pipe and pipe fittings.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

            - Childers Brand, Specialty Construction Brands, Inc., a business of H. B. Fuller Company; Chil-Glas Number 10.

            - Approved equal.

        - Woven Polyester Fabric:  Approximately 1 oz./sq. yd. (34 g/sq. m) with a thread count of 10 strands by 10 strands/sq. in. (4 strands by 4 strands/sq. mm), in a Leno weave, for pipe.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

            - Foster Brand, Specialty Construction Brands, Inc., a business of H. B. Fuller Company; Mast-A-Fab.

            - Vimasco Corporation; Elastafab 894.

            - b.	Approved equal .

      - FIELD-APPLIED CLOTHS

        - Woven Glass-Fiber Fabric:  Comply with MIL-C-20079H, Type I, plain weave, and presized a minimum of 8 oz./sq. yd. (271 g/sq. m).

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

            - Alpha Associates, Inc.; Alpha-Maritex 84215 and 84217/9485RW, Luben 59.

            - Approved equal.

      - TAPES

Product performance is based on products manufactured by Venture Tape; there are slight variations among manufacturers.

        - ASJ Tape:  White vapor-retarder tape matching factory-applied jacket with acrylic adhesive, complying with ASTM C 1136.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

            - ABI, Ideal Tape Division; 428 AWF ASJ.

            - Avery Dennison Corporation, Specialty Tapes Division; Fasson 0836.

            - Compac Corporation; 104 and 105.

            - Venture Tape; 1540 CW Plus, 1542 CW Plus, and 1542 CW Plus/SQ.

            - Approved equal.

          - Width:  3 inches.

          - Thickness:  11.5 mils.

          - Adhesion:  90 ounces force/inch (1.0 N/mm) in width.

          - Elongation:  2 percent.

          - Tensile Strength:  40 lbf/inch in width.

          - ASJ Tape Disks and Squares:  Precut disks or squares of ASJ tape.

        - FSK Tape:  Foil-face, vapor-retarder tape matching factory-applied jacket with acrylic adhesive; complying with ASTM C 1136.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements available products that may be incorporated into the Work include, but are not limited to, the following:

            - ABI, Ideal Tape Division; 491 AWF FSK.

            - Avery Dennison Corporation, Specialty Tapes Division; Fasson 0827.

            - Compac Corporation; 110 and 111.

            - Venture Tape; 1525 CW NT, 1528 CW, and 1528 CW/SQ.

            - Approved equal.

          - Width:  3 inches (75 mm).

          - Thickness:  6.5 mils (0.16 mm).

          - Adhesion:  90 ounces force/inch (1.0 N/mm) in width.

          - Elongation:  2 percent.

          - Tensile Strength:  40 lbf/inch (7.2 N/mm) in width.

          - FSK Tape Disks and Squares:  Precut disks or squares of FSK tape.

        - Aluminum-Foil Tape:  Vapor-retarder tape with acrylic adhesive.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements, available products that may be incorporated into the Work include, but are not limited to, the following:

            - ABI, Ideal Tape Division; 488 AWF.

            - Avery Dennison Corporation, Specialty Tapes Division; Fasson 0800.

            - Compac Corporation; 120.

            - Venture Tape; 3520 CW.

            - Approved equal.

          - Width:  2 inches (50 mm).

          - Thickness:  3.7 mils (0.093 mm).

          - Adhesion:  100 ounces force/inch (1.1 N/mm) in width.

          - Elongation:  5 percent.

          - Tensile Strength:  34 lbf/inch (6.2 N/mm) in width.

      - PROTECTIVE SHIELDING GUARDS

        - Protective Shielding Pipe Covers:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

          - Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

            - Engineered Brass Company.

            - Insul-Tect Products Co.; a subsidiary of MVG Molded Products.

            - McGuire Manufacturing.

            - Plumberex.

            - Truebro; a brand of IPS Corporation.

            - Zurn Industries, LLC; Tubular Brass Plumbing Products Operation.

            - Approved equal.

          - Description:  Manufactured plastic wraps for covering plumbing fixture hot- and cold-water supplies and trap and drain piping.  Comply with Americans with Disabilities Act (ADA) requirements.

        - Protective Shielding Piping Enclosures:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

          - Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

            - Truebro; a brand of IPS Corporation.

            - Zurn Industries, LLC; Tubular Brass Plumbing Products Operation.

            - Approved equal.

          - Description:  Manufactured plastic enclosure for covering plumbing fixture hot- and cold-water supplies and trap and drain piping.  Comply with ADA requirements.

- EXECUTION

      - EXAMINATION

        - Examine substrates and conditions for compliance with requirements for installation tolerances and other conditions affecting performance of insulation application.

          - Verify that systems to be insulated have been tested and are free of defects.

          - Verify that surfaces to be insulated are clean and dry.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - PREPARATION

Retain one of first two paragraphs below.  Corrosion of pipe under insulation, while not typically caused by insulation, is an issue that must be considered during design of any plumbing insulation system.  The potential for corrosion depends on many factors.  Requirements cited in second paragraph represent added measures of protection but are not meant to take the place of proper system design and specification.

        - Surface Preparation:  Clean and dry surfaces to receive insulation.  Remove materials that will adversely affect insulation application.

        - Surface Preparation:  Clean and prepare surfaces to be insulated.  Before insulating, apply a corrosion coating to insulated surfaces as follows:

          - Stainless Steel:  Coat 300 series stainless steel with an epoxy primer 5 mils (0.127 mm) thick and an epoxy finish 5 mils (0.127 mm) thick if operating in a temperature range between 140 and 300 deg F (60 and 149 deg C).  Consult coating manufacturer for appropriate coating materials and application methods for operating temperature range.

          - Carbon Steel:  Coat carbon steel operating at a service temperature between 32 and 300 deg F (0 and 149 deg C) with an epoxy coating.  Consult coating manufacturer for appropriate coating materials and application methods for operating temperature range.

        - Coordinate insulation installation with the trade installing heat tracing.  Comply with requirements for heat tracing that apply to insulation.

        - Mix insulating cements with clean potable water; if insulating cements are to be in contact with stainless-steel surfaces, use demineralized water.

      - GENERAL INSTALLATION REQUIREMENTS

        - Install insulation materials, accessories, and finishes with smooth, straight, and even surfaces; free of voids throughout the length of piping including fittings, valves, and specialties.

        - Install insulation materials, forms, vapor barriers or retarders, jackets, and thicknesses required for each item of pipe system as specified in insulation system schedules.

        - Install accessories compatible with insulation materials and suitable for the service.  Install accessories that do not corrode, soften, or otherwise attack insulation or jacket in either wet or dry state.

        - Install insulation with longitudinal seams at top and bottom of horizontal runs.

        - Install multiple layers of insulation with longitudinal and end seams staggered.

        - Do not weld brackets, clips, or other attachment devices to piping, fittings, and specialties.

        - Keep insulation materials dry during application and finishing.

        - Install insulation with tight longitudinal seams and end joints.  Bond seams and joints with adhesive recommended by insulation material manufacturer.

        - Install insulation with least number of joints practical.

        - Where vapor barrier is indicated, seal joints, seams, and penetrations in insulation at hangers, supports, anchors, and other projections with vapor-barrier mastic.

          - Install insulation continuously through hangers and around anchor attachments.

          - For insulation application where vapor barriers are indicated, extend insulation on anchor legs from point of attachment to supported item to point of attachment to structure.  Taper and seal ends at attachment to structure with vapor-barrier mastic.

          - Install insert materials and install insulation to tightly join the insert.  Seal insulation to insulation inserts with adhesive or sealing compound recommended by insulation material manufacturer.

          - Cover inserts with jacket material matching adjacent pipe insulation.  Install shields over jacket, arranged to protect jacket from tear or puncture by hanger, support, and shield.

        - Apply adhesives, mastics, and sealants at manufacturer's recommended coverage rate and wet and dry film thicknesses.

        - Install insulation with factory-applied jackets as follows:

          - Draw jacket tight and smooth.

          - Cover circumferential joints with 3-inch- (75-mm-) wide strips, of same material as insulation jacket.  Secure strips with adhesive and outward clinching staples along both edges of strip, spaced 4 inches (100 mm) o.c.

          - Overlap jacket longitudinal seams at least 1-1/2 inches (38 mm).  Install insulation with longitudinal seams at bottom of pipe.  Clean and dry surface to receive self-sealing lap.  Staple laps with outward clinching staples along edge at 2 inches o.c.

            - For below-ambient services, apply vapor-barrier mastic over staples.

          - Cover joints and seams with tape, according to insulation material manufacturer's written instructions, to maintain vapor seal.

          - Where vapor barriers are indicated, apply vapor-barrier mastic on seams and joints and at ends adjacent to pipe flanges and fittings.

        - Cut insulation in a manner to avoid compressing insulation more than 75 percent of its nominal thickness.

        - Finish installation with systems at operating conditions.  Repair joint separations and cracking due to thermal movement.

        - Repair damaged insulation facings by applying same facing material over damaged areas.  Extend patches at least 4 inches (100 mm) beyond damaged areas.  Adhere, staple, and seal patches similar to butt joints.

        - For above-ambient services, do not install insulation to the following:

          - Vibration-control devices.

          - Testing agency labels and stamps.

          - Nameplates and data plates.

          - Cleanouts.

      - PENETRATIONS

        - Insulation Installation at Interior Wall and Partition Penetrations (That Are Not Fire Rated):  Install insulation continuously through walls and partitions.

        - Insulation Installation at Fire-Rated Wall and Partition Penetrations:  Install insulation continuously through penetrations of fire-rated walls and partitions.

          - Comply with requirements in Division 07 Section "Penetration Firestopping" for firestopping and fire-resistive joint sealers.

      - GENERAL PIPE INSULATION INSTALLATION

        - Requirements in this article generally apply to all insulation materials except where more specific requirements are specified in various pipe insulation material installation articles.

Where pipe expansion is anticipated, detail expansion compensation for insulation on Drawings and indicate intervals for its occurrence.  See the Midwest Insulation Contractors Association's "National Commercial & Industrial Insulation Standards," Plate No. 41A.

        - Insulation Installation on Fittings, Valves, Strainers, Flanges, and Unions:

          - Install insulation over fittings, valves, strainers, flanges, unions, and other specialties with continuous thermal and vapor-retarder integrity unless otherwise indicated.

          - Insulate pipe elbows using preformed fitting insulation or mitered fittings made from same material and density as adjacent pipe insulation.  Each piece shall be butted tightly against adjoining piece and bonded with adhesive.  Fill joints, seams, voids, and irregular surfaces with insulating cement finished to a smooth, hard, and uniform contour that is uniform with adjoining pipe insulation.

          - Insulate tee fittings with preformed fitting insulation or sectional pipe insulation of same material and thickness as used for adjacent pipe.  Cut sectional pipe insulation to fit.  Butt each section closely to the next and hold in place with tie wire.  Bond pieces with adhesive.

          - Insulate valves using preformed fitting insulation or sectional pipe insulation of same material, density, and thickness as used for adjacent pipe.  Overlap adjoining pipe insulation by not less than two times the thickness of pipe insulation, or one pipe diameter, whichever is thicker.  For valves, insulate up to and including the bonnets, valve stuffing-box studs, bolts, and nuts.  Fill joints, seams, and irregular surfaces with insulating cement.

          - Insulate strainers using preformed fitting insulation or sectional pipe insulation of same material, density, and thickness as used for adjacent pipe.  Overlap adjoining pipe insulation by not less than two times the thickness of pipe insulation, or one pipe diameter, whichever is thicker.  Fill joints, seams, and irregular surfaces with insulating cement.  Insulate strainers so strainer basket flange or plug can be easily removed and replaced without damaging the insulation and jacket.  Provide a removable reusable insulation cover.  For below-ambient services, provide a design that maintains vapor barrier.

          - Insulate flanges and unions using a section of oversized preformed pipe insulation.  Overlap adjoining pipe insulation by not less than two times the thickness of pipe insulation, or one pipe diameter, whichever is thicker.

          - Cover segmented insulated surfaces with a layer of finishing cement and coat with a mastic.  Install vapor-barrier mastic for below-ambient services and a breather mastic for above-ambient services.  Reinforce the mastic with fabric-reinforcing mesh.  Trowel the mastic to a smooth and well-shaped contour.

          - Stencil or label the outside insulation jacket of each union with the word "union."  Match size and color of pipe labels.

Coordinate paragraph below with Drawings.

        - Install removable insulation covers at locations indicated.  Installation shall conform to the following:

          - Make removable flange and union insulation from sectional pipe insulation of same thickness as that on adjoining pipe.  Install same insulation jacket as adjoining pipe insulation.

          - When flange and union covers are made from sectional pipe insulation, extend insulation from flanges or union long at least two times the insulation thickness over adjacent pipe insulation on each side of flange or union.  Secure flange cover in place with stainless-steel or aluminum bands.  Select band material compatible with insulation and jacket.

          - Construct removable valve insulation covers in same manner as for flanges, except divide the two-part section on the vertical center line of valve body.

          - When covers are made from block insulation, make two halves, each consisting of mitered blocks wired to stainless-steel fabric.  Secure this wire frame, with its attached insulation, to flanges with tie wire.  Extend insulation at least 2 inches (50 mm) over adjacent pipe insulation on each side of valve.  Fill space between flange or union cover and pipe insulation with insulating cement.  Finish cover assembly with insulating cement applied in two coats.  After first coat is dry, apply and trowel second coat to a smooth finish.

      - INSTALLATION OF CELLULAR-GLASS INSULATION

        - Insulation Installation on Straight Pipes and Tubes:

          - Secure each layer of insulation to pipe with wire or bands and tighten bands without deforming insulation materials.

          - Where vapor barriers are indicated, seal longitudinal seams, end joints, and protrusions with vapor-barrier mastic and joint sealant.

          - For insulation with factory-applied jackets on above-ambient services, secure laps with outward clinched staples at 6 inches (150 mm) o.c.

          - For insulation with factory-applied jackets on below-ambient services, do not staple longitudinal tabs.  Instead, secure tabs with additional adhesive as recommended by insulation material manufacturer and seal with vapor-barrier mastic and flashing sealant.

        - Insulation Installation on Pipe Flanges:

          - Install preformed pipe insulation to outer diameter of pipe flange.

          - Make width of insulation section same as overall width of flange and bolts, plus twice the thickness of pipe insulation.

          - Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with cut sections of cellular-glass block insulation of same thickness as pipe insulation.

          - Install jacket material with manufacturer's recommended adhesive, overlap seams at least 1 inch (25 mm), and seal joints with flashing sealant.

        - Insulation Installation on Pipe Fittings and Elbows:

          - Install preformed sections of same material as straight segments of pipe insulation when available.  Secure according to manufacturer's written instructions.

          - When preformed sections of insulation are not available, install mitered sections of cellular-glass insulation.  Secure insulation materials with wire or bands.

        - Insulation Installation on Valves and Pipe Specialties:

          - Install preformed sections of cellular-glass insulation to valve body.

          - Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation.

          - Install insulation to flanges as specified for flange insulation application.

      - INSTALLATION OF MINERAL-FIBER INSULATION

        - Insulation Installation on Straight Pipes and Tubes:

          - Secure each layer of preformed pipe insulation to pipe with wire or bands and tighten bands without deforming insulation materials.

          - Where vapor barriers are indicated, seal longitudinal seams, end joints, and protrusions with vapor-barrier mastic and joint sealant.

          - For insulation with factory-applied jackets on above-ambient surfaces, secure laps with outward clinched staples at 6 inches (150 mm) o.c.

          - For insulation with factory-applied jackets on below-ambient surfaces, do not staple longitudinal tabs.  Instead, secure tabs with additional adhesive as recommended by insulation material manufacturer and seal with vapor-barrier mastic and flashing sealant.

        - Insulation Installation on Pipe Flanges:

          - Install preformed pipe insulation to outer diameter of pipe flange.

          - Make width of insulation section same as overall width of flange and bolts, plus twice the thickness of pipe insulation.

          - Fill voids between inner circumference of flange insulation and outer circumference of adjacent straight pipe segments with mineral-fiber blanket insulation.

          - Install jacket material with manufacturer's recommended adhesive, overlap seams at least 1 inch (25 mm), and seal joints with flashing sealant.

        - Insulation Installation on Pipe Fittings and Elbows:

          - Install preformed sections of same material as straight segments of pipe insulation when available.

          - When preformed insulation elbows and fittings are not available, install mitered sections of pipe insulation, to a thickness equal to adjoining pipe insulation.  Secure insulation materials with wire or bands.

        - Insulation Installation on Valves and Pipe Specialties:

          - Install preformed sections of same material as straight segments of pipe insulation when available.

          - When preformed sections are not available, install mitered sections of pipe insulation to valve body.

          - Arrange insulation to permit access to packing and to allow valve operation without disturbing insulation.

          - Install insulation to flanges as specified for flange insulation application.

      - FIELD-APPLIED JACKET INSTALLATION

        - Where glass-cloth jackets are indicated, install directly over bare insulation or insulation with factory-applied jackets.

          - Draw jacket smooth and tight to surface with 2-inch (50-mm) overlap at seams and joints.

          - Embed glass cloth between two 0.062-inch- (1.6-mm-) thick coats of lagging adhesive.

          - Completely encapsulate insulation with coating, leaving no exposed insulation.

        - Where FSK jackets are indicated, install as follows:

          - Draw jacket material smooth and tight.

          - Install lap or joint strips with same material as jacket.

          - Secure jacket to insulation with manufacturer's recommended adhesive.

          - Install jacket with 1-1/2-inch (38-mm) laps at longitudinal seams and 3-inch- (75-mm-) wide joint strips at end joints.

          - Seal openings, punctures, and breaks in vapor-retarder jackets and exposed insulation with vapor-barrier mastic.

        - Where PVC jackets are indicated, install with 1-inch (25-mm) overlap at longitudinal seams and end joints.  Seal with manufacturer's recommended adhesive.

          - Apply two continuous beads of adhesive to seams and joints, one bead under lap and the finish bead along seam and joint edge.

        - Where metal jackets are indicated, install with 2-inch (50-mm) overlap at longitudinal seams and end joints.  Overlap longitudinal seams arranged to shed water.  Seal end joints with weatherproof sealant recommended by insulation manufacturer.  Secure jacket with stainless-steel bands 12 inches (300 mm) o.c. and at end joints.

      - FINISHES

Coordinate first paragraph below with Division 09 painting Sections.  If specifying PVC jackets, consult jacket manufacturers to determine suitable paint products and revise painting Sections to suit Project.

        - Insulation with ASJ, Glass-Cloth, or Other Paintable Jacket Material:  Paint jacket with paint system identified below and as specified in Division 09 painting Sections.

Retain paint system in subparagraph below for a flat, latex-emulsion size over insulation covering an exterior that is subject to normal use and moderate environments.

          - Flat Acrylic Finish:  Two finish coats over a primer that is compatible with jacket material and finish coat paint.  Add fungicidal agent to render fabric mildew proof.

            - Finish Coat Material:  Interior, flat, latex-emulsion size.

        - Flexible Elastomeric Thermal Insulation:  After adhesive has fully cured, apply two coats of insulation manufacturer's recommended protective coating.

        - Color:  Final color as selected by Architect.  Vary first and second coats to allow visual inspection of the completed Work.

        - Do not field paint aluminum or stainless-steel jackets.

Materials and thicknesses in schedules below are for single-layer applications.  If multilayer applications are needed, insert additional requirements.

      - PIPING INSULATION SCHEDULE, GENERAL

        - Acceptable preformed pipe and tubular insulation materials and thicknesses are identified for each piping system and pipe size range.  If more than one material is listed for a piping system, selection from materials listed is Contractor's option.

        - Items Not Insulated:  Unless otherwise indicated, do not install insulation on the following:

          - Chrome-plated pipes and fittings unless there is a potential for personnel injury.

Piping insulation schedules in first three articles below specify commonly used insulation materials and thicknesses by pipe size range for each service.  LEED Prerequisite EA 2 requires that pipe insulation thickness comply with ASHRAE/IESNA 90.1 table titled "Minimum Pipe Insulation Thickness."  Not all materials and thicknesses may be suitable for a specific project.  Revise to suit Project after considering all parameters that impact selection.  Do not duplicate requirements inserted in "Insulation Materials" Article.  See Evaluations for more information and guidance.

Because cellular glass is brittle, the minimum thickness recommended is 1-1/2 inches (38 mm).  Potential for breakage increases if thinner insulation is used.

Tubular flexible elastomeric is not available in sizes larger than NPS 6 (DN 150).  Larger pipe sizes require sheets to be cut to size.  Thickness is limited to 1 inch (25 mm) to meet a flame-spread index of 25 and a smoke-developed index of 50.  Condensation control and energy efficiency are limited by thickness.

Tubular polyolefin is not available in sizes larger than NPS 4 (DN 100).  Larger pipe sizes require sheets to be cut to size.  Thickness is limited to 1 inch (25 mm) to meet a flame-spread index of 25 and a smoke-developed index of 50.  Condensation control and energy efficiency are limited by thickness.

      - INDOOR PIPING INSULATION SCHEDULE

See the Insulation Evaluation tables in the Evaluations for rankings of different insulation types for different service ranges.

Retain "one of" option in subparagraphs below to allow Contractor to select piping materials from those retained.

Evaluate the need to insulate domestic water for condensation and sound control.

        - Domestic Cold Water:

          - NPS 1 and Smaller:  Insulation shall be one of the following:

Retain one or more of five subparagraphs below.

            - Cellular Glass:  1-1/2 inches thick.

            - Mineral-Fiber, Preformed Pipe Insulation, Type I:  1 inch thick.

        - Domestic Hot including Hot Water Dispenser Water:

          - NPS 1-1/4 and Smaller:  Insulation shall be one of the following:

Retain one or more of five subparagraphs below.

            - Cellular Glass:  1-1/2 inches thick.

            - Mineral-Fiber, Preformed Pipe Insulation, Type I:  1 inch thick.

Retain first paragraph below for personnel protection.

        - Exposed Sanitary Drains, Domestic Water, Domestic Hot Water, and Stops for Plumbing Fixtures for People with Disabilities:

          - All Pipe Sizes:  Insulation shall be one of the following:

Retain one or more of three subparagraphs below.

            - Mineral-Fiber, Preformed Pipe Insulation, Type I: 1/2 inch thick.

        - Floor Drains, Traps, and Sanitary Drain Piping within 10 Feet of Drain Receiving Condensate and Equipment Drain Water below 60 Deg F (16 Deg C):

          - All Pipe Sizes:  Insulation shall be one of the following:

Retain one or more of five subparagraphs below.

            - Cellular Glass: 1-1/2 inches thick.

            - Mineral-Fiber, Preformed Pipe Insulation, Type I:  1 inch thick.

        - Hot Service Drains:

          - All Pipe Sizes:  Insulation shall be one of the following:

Retain one or both subparagraphs below.

            - Cellular Glass: 1-1/2 inches thick.

            - Mineral-Fiber, Preformed Pipe, Type I or II:  1 inch thick.

        - Sink Pump Discharge Pipe:

          - All Pipe Sizes:  Insulation shall be one of the following:

Retain one or both subparagraphs below.

            - Cellular Glass:  1” thick.

            - Mineral-Fiber, Preformed Pipe, Type I or II:  1/2" inch thick.

END OF SECTION 220719