Copyright 2006 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 221116 - DOMESTIC WATER PIPING

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Aboveground domestic water pipes, tubes, fittings, and specialties inside the building.

          - Encasement for piping.

          - Specialty valves.

          - Flexible connectors.

Retain one of two subparagraphs below; delete both if water meters are furnished and installed by the utility company.

      - PERFORMANCE REQUIREMENTS

Revise this article to indicate specific loads determined by Project's structural engineer or see loads indicated on Drawings.  Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions.  Verify requirements of authorities having jurisdiction.

        - Seismic Performance:  Domestic water piping and support and installation shall withstand effects of earthquake motions determined according to ASCE/SEI 7.

      - SUBMITTALS

First two paragraphs below are defined in Division 01 Section "Submittal Procedures" as "Action Submittals."

        - Product Data:  For the following products:

          - Specialty valves.

          - Transition fittings.

          - Dielectric fittings.

          - Flexible connectors.

Retain first subparagraph below if water meters are furnished and installed by Contractor.

Remaining paragraphs are defined in Division 01 Section "Submittal Procedures" as "Informational Submittals."

        - Field quality-control reports.

      - QUALITY ASSURANCE

        - Piping materials shall bear label, stamp, or other markings of specified testing agency.

Retain first paragraph below if plastic piping materials are retained.

        - Comply with NSF 14 for plastic, potable domestic water piping and components.

        - Comply with NSF 61 for potable domestic water piping and components.

      - PROJECT CONDITIONS

Retain this article if interruption of existing water service is required.

        - Interruption of Existing Water Service:  Do not interrupt water service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary water service according to requirements indicated:

          - Notify Owner no fewer than two days in advance of proposed interruption of water service.

          - Do not proceed with interruption of water service without Owner's written permission.

      - COORDINATION

Retain this article if large water meters will be mounted on concrete bases.

        - Coordinate sizes and locations of concrete bases with actual equipment provided.

- PRODUCTS

      - PIPING MATERIALS

See "Writing Guide" Article in the Evaluations for a discussion of how this Section is organized and the most efficient way to edit this Section.  See "Piping Materials and Standards" Article in the Evaluations for a discussion of piping materials covered by referenced standards.

        - Comply with requirements in "Piping Schedule" Article for applications of pipe, tube, fitting materials, and joining methods for specific services, service locations, and pipe sizes.

      - COPPER TUBE AND FITTINGS

Tube in first paragraph below is available in NPS 1/8 to NPS 12 (DN 6 to DN 300).

        - Hard Copper Tube:  ASTM B 88, Type L  water tube, drawn temper.

Fittings in first subparagraph below are available in NPS 1/4 to NPS 12 (DN 8 to DN 300).

          - Cast-Copper Solder-Joint Fittings:  ASME B16.18, pressure fittings.

Fittings in first subparagraph below are available in NPS 1/4 to NPS 8 (DN 8 to DN 200).

          - Wrought-Copper Solder-Joint Fittings:  ASME B16.22, wrought-copper pressure fittings.

Flanges in first subparagraph below are available in NPS 1/2 to NPS 12 (DN 15 to DN 300).

          - Bronze Flanges:  ASME B16.24, Class 150, with solder-joint ends.

Unions in first subparagraph below are available in NPS 1/4 to NPS 4 (DN 8 to DN 100).

          - Copper Unions:  MSS SP-123, cast-copper-alloy, hexagonal-stock body, with ball-and-socket, metal-to-metal seating surfaces, and solder-joint or threaded ends.

Fittings in first subparagraph below are available in NPS 1/2 to NPS 4 (DN 15 to DN 100).

          - Copper Pressure-Seal-Joint Fittings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

            - Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

              - Elkhart Products Corporation; Industrial Division.

              - NIBCO INC.

              - Viega; Plumbing and Heating Systems.

              - Approved equal.

            - NPS 2 and Smaller:  Wrought-copper fitting with EPDM-rubber O-ring seal in each end.

Fittings in first subparagraph below are available in NPS 1/2 to NPS 2 (DN 15 to DN 50).

Extruded-tee connections in first subparagraph below can be used instead of tee fittings in copper tubing;  delete if prohibited.

          - Copper-Tube Extruded-Tee Connections:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

            - Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

              - T-DRILL Industries Inc.

              - Approved equal.

            - Description:  Tee formed in copper tube according to ASTM F 2014.

          - Grooved-Joint Copper-Tube Appurtenances:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

            - Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

              - Anvil International.

              - Shurjoint Piping Products.

              - Victaulic Company.

              - Approved equal.

            - Copper Grooved-End Fittings:  ASTM B 75 copper tube or ASTM B 584 bronze castings.

AWWA C606 does not cover couplings in subparagraph below for grooved-end copper tubing.  At least one manufacturer makes this type of coupling with dimensions for copper tube and fittings.  Another manufacturer listed has a system for expanding the ends of copper tube and fittings so couplings for steel piping may be used.

            - Grooved-End-Tube Couplings:  Copper-tube dimensions and design similar to AWWA C606.  Include ferrous housing sections, EPDM-rubber gaskets suitable for hot and cold water, and bolts and nuts.

Tube in paragraph below is available in NPS 1/8 to NPS 12 (DN 6 to DN 300).

      - PIPING JOINING MATERIALS

        - Pipe-Flange Gasket Materials:  AWWA C110, rubber, flat face, 1/8 inch thick or ASME B16.21, nonmetallic and asbestos free, unless otherwise indicated; full-face or ring type unless otherwise indicated.

        - Metal, Pipe-Flange Bolts and Nuts:  ASME B18.2.1, carbon steel unless otherwise indicated.

        - Solder Filler Metals:  ASTM B 32, lead-free alloys.  Include water-flushable flux according to ASTM B 813.

        - Brazing Filler Metals:  AWS A5.8/A5.8M, BCuP Series, copper-phosphorus alloys for general-duty brazing unless otherwise indicated.

      - SPECIALTY VALVES

Caution:  MSS SP-122 is a standard for plastic ball valves, but it is not comprehensive and additional data may be required for certain applications.  In general, end types and pressure and temperature ratings are required.  No applicable standards are available for plastic butterfly or check valves.  CPVC and PEX piping in this Section are rated for up to 180 deg F (82 deg C).  This Section assumes a maximum operating temperature of 140 deg F (60 deg C) for domestic water piping.  Verify that plastic valves are adequate for operating temperature of piping systems in this Project.

MSS SP-122 covers plastic ball valves in first paragraph below in NPS 1/4 to NPS 4 (DN 8 to DN 100).  Verify that valve selections are available from manufacturers retained.

        - Full Port Ball Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

          - Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

            - Apollo 77-4100 (Basis of Design).

            - NIBCO INC.

            - Jamesbury.

            - Approved equal.

          - Description:

            - Standard:  MSS SP-110.

            - Pressure Rating:  600 psi CWP.

            - Body Material:  Bronze.

            - Body Design:  Two Piece.

            - End Connections for Valves NPS 2 (DN 50) and Smaller:  Detachable, threaded.

            - Ball:  Bronze chrome plated.

            - Seals:  RPTFE.

            - Handle:  Lever.

Valves in first paragraph below are available in NPS 1/4 to NPS 4 (DN 8 to DN 100).  Verify that valve selections are available from manufacturers retained.

        - PVC Ball Check Valves:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

          - Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

            - American Valve, Inc.

            - Asahi/America, Inc.

            - Colonial Engineering, Inc.

            - Fischer, George Inc.

            - Hayward Flow Control Systems; Hayward Industrial Products, Inc.

            - IPEX Inc.

            - Legend Valve.

            - NIBCO INC.

            - Sloane, George Fischer, Inc.

            - Spears Manufacturing Company.

            - Thermoplastic Valves Inc.

            - Approved equal.

          - Description:

            - Pressure Rating:  125 psig at 73 deg F.

            - Body Material:  PVC.

            - Body Design:  Union-type ball check.

            - End Connections for Valves NPS 2 (DN 50) and Smaller:  Detachable, socket or threaded.

      - TRANSITION FITTINGS

        - General Requirements:

          - Same size as pipes to be joined.

          - Pressure rating at least equal to pipes to be joined.

          - End connections compatible with pipes to be joined.

        - Fitting-Type Transition Couplings:  Manufactured piping coupling or specified piping system fitting.

Couplings in first paragraph below are available in NPS 1/2 to NPS 144 (DN 15 to DN 3600).

        - Sleeve-Type Transition Coupling:  AWWA C219.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

          - Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

            - Cascade Waterworks Manufacturing.

            - Dresser, Inc.; Dresser Piping Specialties.

            - Ford Meter Box Company, Inc. (The).

            - JCM Industries.

            - Romac Industries, Inc.

            - Smith-Blair, Inc; a Sensus company.

            - Viking Johnson; c/o Mueller Co.

            - Approved equal.

Fittings in first paragraph below are available in at least NPS 1/2 to NPS 2 (DN 15 to DN 50).

        - Plastic-to-Metal Transition Fittings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

          - Manufacturers:  Subject to compliance with requirements available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

            - Charlotte Pipe and Foundry Company.

            - Harvel Plastics, Inc.

            - Spears Manufacturing Company.

            - Approved equal.

          - Description PVC one-piece fitting with manufacturer's Schedule 80 equivalent dimensions; one end with threaded brass insert and one solvent-cement-socket or threaded end.

Unions in paragraph below are available in NPS 1/2 to NPS 4 (DN 15 to DN 100).

        - Plastic-to-Metal Transition Unions:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

          - Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

            - Colonial Engineering, Inc.

            - NIBCO INC.

            - Spears Manufacturing Company.

            - Approved equal.

          - Description:  PVC four-part union.  Include brass[ or stainless-steel] threaded end, solvent-cement-joint or threaded plastic end, rubber O-ring, and union nut.

      - DIELECTRIC FITTINGS

        - General Requirements:  Assembly of copper alloy and ferrous materials or ferrous material body with separating nonconductive insulating material suitable for system fluid, pressure, and temperature.

Unions in first paragraph below are available in at least NPS 1/2 to NPS 2 (DN 15 to DN 50).

        - Dielectric Unions:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

          - Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

            - Capitol Manufacturing Company.

            - Central Plastics Company.

            - EPCO Sales, Inc.

            - Hart Industries International, Inc.

            - Watts Regulator Co.; a division of Watts Water Technologies, Inc.

            - Zurn Plumbing Products Group; Wilkins Water Control Products.

            - Approved equal.

          - Description:

Revise pressure rating and temperature in first subparagraph below to suit Project, or insert other options for specific applications.

            - Pressure Rating: 150 psig at 180 deg F (82 deg C).

            - End Connections:  Solder-joint copper alloy and threaded ferrous.

Flanges in first paragraph below are available in at least NPS 1-1/2 to NPS 4 (DN 40 to DN 100).

      - FLEXIBLE CONNECTORS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

        - Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

          - Flex-Hose Co., Inc.

          - Flexicraft Industries.

          - Flex Pression, Ltd.

          - Flex-Weld, Inc.

          - Hyspan Precision Products, Inc.

          - Mercer Rubber Co.

          - Metraflex, Inc.

          - Proco Products, Inc.

          - Tozen Corporation.

          - Unaflex, Inc.

          - Universal Metal Hose; a Hyspan company

          - Approved equal.

        - Bronze-Hose Flexible Connectors:  Corrugated-bronze tubing with bronze wire-braid covering and ends brazed to inner tubing.

          - Working-Pressure Rating:  Minimum 200 psig.

          - End Connections NPS 2 (DN 50) and Smaller:  Threaded copper pipe or plain-end copper tube.

          - End Connections NPS 2-1/2 (DN 65) and Larger:  Flanged copper alloy.

        - Stainless-Steel-Hose Flexible Connectors:  Corrugated-stainless-steel tubing with stainless-steel wire-braid covering and ends welded to inner tubing.

          - Working-Pressure Rating:  Minimum 200 psig.

          - End Connections NPS 2 (DN 50) and Smaller:  Threaded steel-pipe nipple.

          - End Connections NPS 2-1/2 (DN 65) and Larger:  Flanged steel nipple.

- EXECUTION

      - PIPING INSTALLATION

See "Writing Guide" Article in the Evaluations for a discussion of how this Section is organized and the most efficient way to edit this Section.

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified.  If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Drawing plans, schematics, and diagrams indicate general location and arrangement of domestic water piping.  Indicated locations and arrangements are used to size pipe and calculate friction loss, expansion, and other design considerations.  Install piping as indicated unless deviations to layout are approved on Coordination Drawings.

        - Install shutoff valve immediately upstream of each dielectric fitting.

Retain first paragraph below if booster pumps are not required.

        - Install domestic water piping level without pitch and plumb.

Retain first paragraph below if water meters are inside the building.

        - Install piping concealed from view and protected from physical contact by building occupants unless otherwise indicated and except in equipment rooms and service areas.

        - Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls.  Diagonal runs are prohibited unless specifically indicated otherwise.

        - Install piping above accessible ceilings to allow sufficient space for ceiling panel removal, and coordinate with other services occupying that space.

        - Install piping adjacent to equipment and specialties to allow service and maintenance.

        - Install piping to permit valve servicing.

        - Install nipples, unions, special fittings, and valves with pressure ratings the same as or higher than system pressure rating used in applications below unless otherwise indicated.

        - Install piping free of sags and bends.

        - Install fittings for changes in direction and branch connections.

        - Install unions in copper tubing at final connection to each piece of equipment, machine, and specialty.

        - Install sleeves for piping penetrations of walls, ceilings, and floors.  Comply with requirements for sleeves specified in Division 22 Section "Sleeves and Sleeve Seals for Plumbing Piping."

Retain first paragraph below for piping that penetrates an exterior concrete wall or concrete slab.

        - Install sleeve seals for piping penetrations of concrete walls and slabs.  Comply with requirements for sleeve seals specified in Division 22 Section "Sleeves and Sleeve Seals for Plumbing Piping."

        - Install escutcheons for piping penetrations of walls, ceilings, and floors.  Comply with requirements for escutcheons specified in Division 22 Section "Escutcheons for Plumbing Piping."

      - JOINT CONSTRUCTION

        - Ream ends of pipes and tubes and remove burrs.  Bevel plain ends of steel pipe.

        - Remove scale, slag, dirt, and debris from inside and outside of pipes, tubes, and fittings before assembly.

        - Threaded Joints:  Thread pipe with tapered pipe threads according to ASME B1.20.1.  Cut threads full and clean using sharp dies.  Ream threaded pipe ends to remove burrs and restore full ID.  Join pipe fittings and valves as follows:

          - Apply appropriate tape or thread compound to external pipe threads.

          - Damaged Threads:  Do not use pipe or pipe fittings with threads that are corroded or damaged.

        - Brazed Joints:  Join copper tube and fittings according to CDA's "Copper Tube Handbook," "Brazed Joints" Chapter.

        - Soldered Joints:  Apply ASTM B 813, water-flushable flux to end of tube.  Join copper tube and fittings according to ASTM B 828 or CDA's "Copper Tube Handbook."

        - Pressure-Sealed Joints:  Join copper tube and pressure-seal fittings with tools recommended by fitting manufacturer.

        - Copper-Tubing, Push-on Joints:  Clean end of tube.  Measure insertion depth with manufacturer's depth gage.  Join copper tube and push-on-joint fittings by inserting tube to measured depth.

        - Extruded-Tee Connections:  Form tee in copper tube according to ASTM F 2014.  Use tool designed for copper tube; drill pilot hole, form collar for outlet, dimple tube to form seating stop, and braze branch tube into collar.

        - Copper-Tubing Grooved Joints:  Roll groove end of tube.  Assemble coupling with housing, gasket, lubricant, and bolts.  Join copper tube and grooved-end fittings according to AWWA C606 for roll-grooved joints.

        - Plastic Piping Solvent-Cement Joints:  Clean and dry joining surfaces.  Join pipe and fittings according to the following:

          - Comply with ASTM F 402 for safe-handling practice of cleaners, primers, and solvent cements.  Apply primer.

          - CPVC Piping:  Join according to ASTM D 2846/D 2846M Appendix.

          - PVC Piping:  Join according to ASTM D 2855.

        - Dissimilar-Material Piping Joints:  Make joints using adapters compatible with materials of both piping systems.

      - VALVE INSTALLATION

        - General-Duty Valves:  Comply with requirements in Division 22 Section "General-Duty Valves for Plumbing Piping" for valve installations.

        - Install shutoff valve close to water main on each branch and riser serving plumbing fixtures or equipment, on each water supply to equipment, and on each water supply to plumbing fixtures that do not have supply stops.  Use full port ball valves for piping NPS 2 (DN 50) and smaller.  Use butterfly or gate valves for piping NPS 2-1/2 (DN 65) and larger.

NPS 1/2 or NPS 3/4 (DN 15 or DN 20) inlet hose-end drain valves may be adequate for application in first paragraph below.

        - Install drain valves for equipment at base of each water riser, at low points in horizontal piping, and where required to drain water piping.  Drain valves shall be full port ball valves.

          - Hose-End Drain Valves:  At low points in water mains, risers, and branches.

          - Stop-and-Waste Drain Valves:  Instead of hose-end drain valves where indicated.

Retain one of two paragraphs below.

      - TRANSITION FITTING INSTALLATION

        - Install transition couplings at joints of dissimilar piping.

        - Transition Fittings in Underground Domestic Water Piping:

          - NPS 1-1/2 (DN 40) and Smaller:  Fitting-type coupling.

          - NPS 2 (DN 50) and Larger:  Sleeve-type coupling.

        - Transition Fittings in Aboveground Domestic Water Piping NPS 2 (DN 50) and Smaller:  Plastic-to-metal transition fittings or unions.

      - DIELECTRIC FITTING INSTALLATION

        - Install dielectric fittings in piping at connections of dissimilar metal piping and tubing.

        - Dielectric Fittings for NPS 2 and Smaller:  Use dielectric couplings or nipples.

      - HANGER AND SUPPORT INSTALLATION

Retain first paragraph below if Project is in a seismic area.

        - Comply with requirements in this Section for pipe hanger and support products and installation.

          - Vertical Piping:  MSS Type 8 or 42, clamps.

          - Individual, Straight, Horizontal Piping Runs:

            - 100 Feet (30 m) and Less:  MSS Type 1, adjustable, steel clevis hangers.

            - Longer than 100 Feet (30 m):  MSS Type 43, adjustable roller hangers.

            - Longer than 100 Feet (30 m) If Indicated:  MSS Type 49, spring cushion rolls.

          - Multiple, Straight, Horizontal Piping Runs 100 Feet (30 m) or Longer:  MSS Type 44, pipe rolls.  Support pipe rolls on trapeze.

          - Base of Vertical Piping:  MSS Type 52, spring hangers.

        - Support vertical piping and tubing at base and at each floor.

        - Rod diameter may be reduced one size for double-rod hangers, to a minimum of 3/8 inch (10 mm).

        - Install hangers for copper tubing with the following maximum horizontal spacing and minimum rod diameters:

          - NPS 3/4 (DN 20) and Smaller:  60 inches (1500 mm) with 3/8-inch (10-mm) rod.

          - NPS 1 and NPS 1-1/4 (DN 25 and DN 32):  72 inches (1800 mm) with 3/8-inch (10-mm) rod.

        - Install supports for vertical copper tubing every 10 feet.

        - Install vinyl-coated hangers for PVC piping with the following maximum horizontal spacing and minimum rod diameters:

          - NPS 2 and Smaller:  48 inches with 3/8-inch rod.

        - Install supports for vertical PVC piping every 48 inches (1200 mm).

        - Support piping and tubing not listed in this article according to MSS SP-69 and manufacturer's written instructions.

      - CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified.  If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Drawings indicate general arrangement of piping, fittings, and specialties.

        - Install piping adjacent to equipment and machines to allow service and maintenance.

        - Connect domestic water piping to exterior water-service piping.  Use transition fitting to join dissimilar piping materials.

        - Connect domestic water piping to water-service piping with shutoff valve; extend and connect to the following:

          - Water Heaters:  Cold-water inlet and hot-water outlet piping in sizes indicated, but not smaller than sizes of water heater connections.

          - Plumbing Fixtures:  Cold- and hot-water supply piping in sizes indicated, but not smaller than required by plumbing code.  Comply with requirements in Division 22 plumbing fixture Sections for connection sizes.

          - Equipment:  Cold- and hot-water supply piping as indicated, but not smaller than equipment connections.  Provide shutoff valve and union for each connection.

      - IDENTIFICATION

        - Identify system components.  Comply with requirements in Division 22 Section "Identification for Plumbing Piping and Equipment" for identification materials and installation.

        - Label pressure piping with system operating pressure.

      - FIELD QUALITY CONTROL

        - Perform tests and inspections.

Retain first paragraph below to describe tests and inspections to be performed.  Portions of testing and inspecting requirements in this article are taken from model plumbing codes.  Verify requirements are applicable to location of this Project.

        - Piping Inspections:

          - Do not enclose, cover, or put piping into operation until it has been inspected and approved by authorities having jurisdiction.

          - During installation, notify authorities having jurisdiction at least one day before inspection must be made.  Perform tests specified below in presence of authorities having jurisdiction:

            - Roughing-in Inspection:  Arrange for inspection of piping before concealing or closing-in after roughing-in and before setting fixtures.

            - Final Inspection:  Arrange final inspection for authorities having jurisdiction to observe tests specified below and to ensure compliance with requirements.

          - Reinspection:  If authorities having jurisdiction find that piping will not pass tests or inspections, make required corrections and arrange for reinspection.

          - Reports:  Prepare inspection reports and have them signed by authorities having jurisdiction.

        - Piping Tests:

          - Fill domestic water piping.  Check components to determine that they are not air bound and that piping is full of water.

          - Test for leaks and defects in new piping and parts of existing piping that have been altered, extended, or repaired.  If testing is performed in segments, submit a separate report for each test, complete with diagram of portion of piping tested.

          - Leave new, altered, extended, or replaced domestic water piping uncovered and unconcealed until it has been tested and approved.  Expose work that was covered or concealed before it was tested.

          - Cap and subject piping to static water pressure of 50 psig (345 kPa) above operating pressure, without exceeding pressure rating of piping system materials.  Isolate test source and allow to stand for four hours.  Leaks and loss in test pressure constitute defects that must be repaired.

          - Repair leaks and defects with new materials and retest piping or portion thereof until satisfactory results are obtained.

          - Prepare reports for tests and for corrective action required.

See Division 01 Section "Quality Requirements" for retesting and reinspecting requirements.  See Division 01 Section "Execution" for requirements for correcting the Work.

        - Domestic water piping will be considered defective if it does not pass tests and inspections.

        - Prepare test and inspection reports.

      - ADJUSTING

        - Perform the following adjustments before operation:

          - Close drain valves, hydrants, and hose bibbs.

          - Open shutoff valves to fully open position.

          - Remove plugs used during testing of piping and for temporary sealing of piping during installation.

          - Remove and clean strainer screens.  Close drain valves and replace drain plugs.

      - CLEANING

Portions of disinfecting requirements in this article are taken from model plumbing codes; revise if requirements vary.  Option in first paragraph below is for disinfection of non-potable domestic water piping.

        - Clean and disinfect potable domestic water piping as follows:

          - Purge new piping and parts of existing piping that have been altered, extended, or repaired before using.

          - Use purging and disinfecting procedures prescribed by authorities having jurisdiction; if methods are not prescribed, use procedures described in either AWWA C651 or AWWA C652 or follow procedures described below:

            - Flush piping system with clean, potable water until dirty water does not appear at outlets.

            - Fill and isolate system according to either of the following:

              - Fill system or part thereof with water/chlorine solution with at least 50 ppm (50 mg/L) of chlorine.  Isolate with valves and allow to stand for 24 hours.

              - Fill system or part thereof with water/chlorine solution with at least 200 ppm (200 mg/L) of chlorine.  Isolate and allow to stand for three hours.

            - Flush system with clean, potable water until no chlorine is in water coming from system after the standing time.

            - Submit water samples in sterile bottles to authorities having jurisdiction.  Repeat procedures if biological examination shows contamination.

Retain first paragraph below if disinfection of non-potable domestic water piping is not required.  If disinfection is required, delete first paragraph below and revise paragraph above.

        - Clean non-potable domestic water piping as follows:

          - Purge new piping and parts of existing piping that have been altered, extended, or repaired before using.

          - Use purging procedures prescribed by authorities having jurisdiction or; if methods are not prescribed, follow procedures described below:

            - Flush piping system with clean, potable water until dirty water does not appear at outlets.

            - Submit water samples in sterile bottles to authorities having jurisdiction.  Repeat procedures if biological examination shows contamination.

        - Prepare and submit reports of purging and disinfecting activities.

        - Clean interior of domestic water piping system.  Remove dirt and debris as work progresses.

      - PIPING SCHEDULE

        - Transition and special fittings with pressure ratings at least equal to piping rating may be used in applications below unless otherwise indicated.

        - Flanges and unions may be used for aboveground piping joints unless otherwise indicated.

Delete first paragraph below if prohibited.

        - Fitting Option:  Extruded-tee connections and brazed joints may be used on aboveground copper tubing.

The "Piping Schedule" Article below is organized to first present the service and pipe size or size range; then to present optional piping materials and joining methods.  Retain the services and sizes and size ranges applicable to the Project, then retain the selected piping materials and joining methods.  Coordinate selection of piping materials and joining methods with piping materials described in Part 2.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.  Piping for this application matches exterior underground water service piping specified in Division 22 Section "Facility Water Distribution Piping."

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

        - Aboveground domestic water piping, NPS 2 and smaller, shall be the following:

          - Hard copper tube, ASTM B 88, Type L; cast- or wrought- copper solder-joint fittings; and soldered joints.

Retain "one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

      - VALVE SCHEDULE

        - Drawings indicate valve types to be used.  Where specific valve types are not indicated, the following requirements apply:

          - Shutoff Duty:  Use full port ball or gate valves for piping NPS 2 and smaller.

          - Drain Duty:  Hose-end drain valves.

        - Use check valves to maintain correct direction of domestic water flow to and from equipment.

Delete paragraph below and use metal valves if temperature rating may be exceeded.  Coordinate selection of "CPVC" or "PVC" option with "Specialty Valves" Article.

        - PVC valves matching piping materials may be used.

END OF SECTION 221116