Copyright 2008 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 221316 - SANITARY WASTE AND VENT PIPING

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Pipe, tube, and fittings.

          - Specialty pipe fittings.

        - Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Division 22 Section "Sanitary Sewerage Pumps" for effluent and sewage pumps.

      - PERFORMANCE REQUIREMENTS

        - Components and installation shall be capable of withstanding the following minimum working pressure unless otherwise indicated:

Revise pressure ratings in two subparagraphs below to suit Project.  Coordinate with Division 22 Section "Sanitary Waste Piping Specialties." Soil and waste piping may require higher rating if used in high-rise buildings.

          - Soil, Waste, and Vent Piping:  10-foot head of water.

          - Waste, Force-Main Piping:  50 psig.

Retain paragraph below with "Seismic Qualification Certificates" Paragraph in "Submittals" Article for Projects requiring seismic design.  Model building codes and ASCE/SEI 7 establish criteria for buildings subject to earthquake motions.  Verify requirements of authorities having jurisdiction.

      - SUBMITTALS

First three paragraphs below are defined in Division 01 Section "Submittal Procedures" as "action submittals."

        - Product Data:  For each type of product indicated.

Retain first paragraph below if a sovent drainage system is retained.

      - QUALITY ASSURANCE

        - Piping materials shall bear label, stamp, or other markings of specified testing agency.

Retain paragraph below if NSF markings are required.

        - Comply with NSF/ANSI 14, "Plastics Piping Systems Components and Related Materials," for plastic piping components.  Include marking with "NSF-dwv" for plastic drain, waste, and vent piping and "NSF-sewer" for plastic sewer piping.

      - PROJECT CONDITIONS

Retain paragraph below if interruption of existing sanitary waste service is required.

        - Interruption of Existing Sanitary Waste Service:  Do not interrupt service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary service according to requirements indicated:

          - Notify Owner no fewer than two days in advance of proposed interruption of sanitary waste service.

          - Do not proceed with interruption of sanitary waste service without Owner's written permission.

- PRODUCTS

      - PIPING MATERIALS

See "Writing Guide" Article in the Evaluations for a discussion of this Section's organization and the most efficient way to revise this Section.  See piping materials articles in the Evaluations for a discussion of piping materials covered by referenced standards.

        - Comply with requirements in "Piping Schedule" Article for applications of pipe, tube, fitting materials, and joining methods for specific services, service locations, and pipe sizes.

      - PVC PIPE AND FITTINGS

Pipe and fittings in first two paragraphs below are available in NPS 1-1/4 to NPS 12 (DN 32 to DN 300).  Retain one or both paragraphs and coordinate with "Piping Schedule" Article.

        - Solid-Wall PVC Pipe:  ASTM D 2665, drain, waste, and vent.

        - Cellular-Core PVC Pipe:  ASTM F 891, Schedule 40.

        - PVC Socket Fittings:  ASTM D 2665, made to ASTM D 3311, drain, waste, and vent patterns and to fit Schedule 40 pipe.

        - Adhesive Primer:  ASTM F 656.

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

          - Use adhesive primer that has a VOC content of 550 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

        - Solvent Cement:  ASTM D 2564.

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

          - Use PVC solvent cement that has a VOC content of 510 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

      - SPECIALTY PIPE FITTINGS

        - Transition Couplings:

          - General Requirements:  Fitting or device for joining piping with small differences in OD's or of different materials.  Include end connections same size as and compatible with pipes to be joined.

Retain pipe couplings in subparagraphs below if dissimilar piping materials or piping with small differences in OD must be joined.

          - Fitting-Type Transition Couplings:  Manufactured piping coupling or specified piping system fitting.

Couplings in first subparagraph below are for underground nonpressure piping and should be available in all sizes.

          - Unshielded, Nonpressure Transition Couplings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

            - Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

              - Dallas Specialty & Mfg. Co.

              - Fernco Inc.

              - Mission Rubber Company; a division of MCP Industries, Inc.

              - Plastic Oddities; a division of Diverse Corporate Technologies, Inc.

              - Approved equal.

            - Standard:  ASTM C 1173.

            - Description:  Elastomeric, sleeve-type, reducing or transition pattern.  Include shear ring and corrosion-resistant-metal tension band and tightening mechanism on each end.

            - Sleeve Materials:

              - For Cast-Iron Soil Pipes:  ASTM C 564, rubber.

              - For Plastic Pipes:  ASTM F 477, elastomeric seal or ASTM D 5926, PVC.

              - For Dissimilar Pipes:  ASTM D 5926, PVC or other material compatible with pipe materials being joined.

Couplings in first subparagraph below are for aboveground nonpressure piping and should be available in most sizes.

Couplings in subparagraph below are for underground pressure piping and are available in at least NPS 1-1/2 to NPS 24 (DN 40 to DN 600).

          - Pressure Transition Couplings:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

            - Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

              - Cascade Waterworks Mfg. Co.

              - Dresser, Inc.

              - EBAA Iron, Inc.

              - JCM Industries, Inc.

              - Romac Industries, Inc.

              - Smith-Blair, Inc.; a Sensus company.

              - The Ford Meter Box Company, Inc.

              - Viking Johnson.

              - Approved equal.

            - Standard:  AWWA C219.

            - Description:  Metal, sleeve-type same size as, with pressure rating at least equal to, and ends compatible with, pipes to be joined.

            - Center-Sleeve Material:  Manufacturer's standard.

            - Gasket Material:  Natural or synthetic rubber.

            - Metal Component Finish:  Corrosion-resistant coating or material.

        - Dielectric Fittings:

          - General Requirements:  Assembly of copper alloy and ferrous materials with separating nonconductive insulating material.  Include end connections compatible with pipes to be joined.

Unions in first subparagraph below are available in at least NPS 1/2 to NPS 2 (DN 15 to DN 50).

          - Dielectric Unions:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

            - Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

              - Capitol Manufacturing Company.

              - Central Plastics Company.

              - Hart Industries International, Inc.

              - Jomar International Ltd.

              - Matco-Norca, Inc.

              - McDonald, A. Y. Mfg. Co.

              - Watts Regulator Co.; a division of Watts Water Technologies, Inc.

              - Wilkins; a Zurn company.

              - Approved equal.

            - Description:

              - Standard:  ASSE 1079.

Revise pressure rating and temperature in first subparagraph below to suit Project, or insert other options for specific applications.

              - Pressure Rating:  125 psig minimum at 180 deg F.

              - End Connections:  Solder-joint copper alloy and threaded ferrous.

Flanges in first subparagraph below are available in at least NPS 1-1/2 to NPS 4 (DN 40 to DN 100).

Nipples in subparagraph below are available in at least NPS 1/2 to NPS 4 (DN 15 to DN 100).

          - Dielectric Nipples:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  See Division 01 Section "Product Requirements."

            - Manufacturers:  Subject to compliance with requirements, available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

              - Elster Perfection.

              - Grinnell Mechanical Products.

              - Matco-Norca, Inc.

              - Precision Plumbing Products, Inc.

              - Victaulic Company.

              - Approved equal.

            - Description:

              - Electroplated steel nipple complying with ASTM F 1545.

Revise pressure rating and temperature in first subparagraph below to suit Project, or insert other options for specific applications.

              - Pressure Rating:  300 psig at 225 deg F.

              - End Connections:  Male threaded or grooved.

              - Lining:  Inert and noncorrosive, propylene.

- EXECUTION

      - PIPING INSTALLATION

See "Writing Guide" Article in the Evaluations for a discussion of how this Section is organized and the most efficient way to revise this Section.

        - Drawing plans, schematics, and diagrams indicate general location and arrangement of piping systems.  Indicated locations and arrangements were used to size pipe and calculate friction loss, expansion, pump sizing, and other design considerations.  Install piping as indicated unless deviations to layout are approved on coordination drawings.

        - Install piping in concealed locations unless otherwise indicated and except in equipment rooms and service areas.

        - Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls.  Diagonal runs are prohibited unless specifically indicated otherwise.

        - Install piping above accessible ceilings to allow sufficient space for ceiling panel removal.

        - Install piping to permit valve servicing.

        - Install piping at indicated slopes.

        - Install piping free of sags and bends.

        - Install fittings for changes in direction and branch connections.

        - Install piping to allow application of insulation.

Retain first paragraph below if piping is required to withstand specific design loads.

        - Make changes in direction for soil and waste drainage and vent piping using appropriate branches, bends, and long-sweep bends.  Sanitary tees and short-sweep 1/4 bends may be used on vertical stacks if change in direction of flow is from horizontal to vertical.  Use long-turn, double Y-branch and 1/8-bend fittings if two fixtures are installed back to back or side by side with common drain pipe.  Straight tees, elbows, and crosses may be used on vent lines.  Do not change direction of flow more than 90 degrees.  Use proper size of standard increasers and reducers if pipes of different sizes are connected.  Reducing size of drainage piping in direction of flow is prohibited.

        - Install soil and waste drainage and vent piping at the following minimum slopes unless otherwise indicated:

Revise three subparagraphs below as required by authorities having jurisdiction.

          - Building Sanitary Drain:  2 percent downward in direction of flow for piping NPS 3 and smaller; 2 percent downward in direction of flow for piping NPS 4 and larger.

          - Horizontal Sanitary Drainage Piping:  2 percent downward in direction of flow.

          - Vent Piping:  1 percent down toward vertical fixture vent or toward vent stack.

        - Install aboveground PVC piping according to ASTM D 2665.

        - Install force mains at elevations indicated.

        - Plumbing Specialties:

          - Install cleanout fitting with closure plug inside the building in sanitary drainage force-main piping.

          - Install drains in sanitary drainage gravity-flow piping.

        - Do not enclose, cover, or put piping into operation until it is inspected and approved by authorities having jurisdiction.

        - Install sleeves for piping penetrations of walls, ceilings, and floors.

Retain first paragraph below for piping that penetrates an exterior concrete wall or concrete slab.

        - Install sleeve seals for piping penetrations of concrete walls and slabs.

        - Install escutcheons for piping penetrations of walls, ceilings, and floors.

      - JOINT CONSTRUCTION

        - Threaded Joints:  Thread pipe with tapered pipe threads according to ASME B1.20.1.  Cut threads full and clean using sharp dies.  Ream threaded pipe ends to remove burrs and restore full ID.  Join pipe fittings and valves as follows:

          - Apply appropriate tape or thread compound to external pipe threads unless dry seal threading is specified.

          - Damaged Threads:  Do not use pipe or pipe fittings with threads that are corroded or damaged.  Do not use pipe sections that have cracked or open welds.

        - Plastic, Nonpressure-Piping, Solvent-Cement Joints:  Clean and dry joining surfaces.  Join pipe and fittings according to the following:

          - Comply with ASTM F 402 for safe-handling practice of cleaners, primers, and solvent cements.

          - PVC Piping:  Join according to ASTM D 2855 and ASTM D 2665 Appendixes.

      - SPECIALTY PIPE FITTING INSTALLATION

        - Transition Couplings:

          - Install transition couplings at joints of piping with small differences in OD's.

          - In Drainage Piping:  Unshielded, nonpressure transition couplings.

          - In Aboveground Force Main Piping:  Fitting-type transition couplings.

        - Dielectric Fittings:

          - Install dielectric fittings in piping at connections of dissimilar metal piping and tubing.

          - Dielectric Fittings for NPS 2  and Smaller:  Use dielectric nipples or unions.

      - VALVE INSTALLATION

Retain this article if valves are required.

        - General valve installation requirements are specified in Division 22 Section "General-Duty Valves for Plumbing Piping."

        - Shutoff Valves:

          - Install shutoff valve on each sewage pump discharge.

          - Install gate or full-port ball valve for piping NPS 2 and smaller.

          - Install gate valve for piping NPS 2-1/2 and larger.

        - Check Valves:  Install ball check valve, between pump and shutoff valve, on sewage pump discharge.

        - Backwater Valves:  Install backwater valves in piping subject to backflow.

          - Horizontal Piping:  Horizontal backwater valves.  Use normally closed type unless otherwise indicated.

          - Install backwater valves in accessible locations.

          - Comply with requirements for backwater valve specified in Division 22 Section "Sanitary Waste Piping Specialties."

      - HANGER AND SUPPORT INSTALLATION

Retain first paragraph below if Project is in seismic area.

        - Comply with requirements for pipe hanger and support devices and installation specified in this Section.

          - Install carbon-steel pipe hangers for horizontal piping in noncorrosive environments.

          - Install carbon-steel pipe support clamps for vertical piping in noncorrosive environments.

          - Vertical Piping:  MSS Type 8 or Type 42, clamps.

          - Install individual, straight, horizontal piping runs:

            - 100 Feet and Less:  MSS Type 1, adjustable, steel clevis hangers.

            - Longer Than 100 Feet:  MSS Type 43, adjustable roller hangers.

            - Longer Than 100 Feet if Indicated:  MSS Type 49, spring cushion rolls.

          - Multiple, Straight, Horizontal Piping Runs 100 Feet or Longer:  MSS Type 44, pipe rolls.  Support pipe rolls on trapeze.

          - Base of Vertical Piping:  MSS Type 52, spring hangers.

        - Support horizontal piping and tubing within 12 inches of each fitting, valve, and coupling.

        - Support vertical piping and tubing at base and at each floor.

        - Rod diameter may be reduced one size for double-rod hangers, with 3/8-inch minimum rods.

Maximum spans in remaining paragraphs were taken from MSS SP-69 for water service and from model plumbing codes.  The most restrictive piping and spacing dimensions allowed are shown.

        - Install hangers for PVC piping with the following maximum horizontal spacing and minimum rod diameters:

          - NPS 1-1/2 and NPS 2 :  48 inches with 3/8-inch rod.

        - Install supports for vertical PVC piping every 48 inches.

        - Support piping and tubing not listed above according to MSS SP-69 and manufacturer's written instructions.

      - CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified.  If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Drawings indicate general arrangement of piping, fittings, and specialties.

        - Connect soil and waste piping to exterior sanitary sewerage piping.  Use transition fitting to join dissimilar piping materials.

        - Connect drainage and vent piping to the following:

Revise first four subparagraphs below to suit Project.

          - Plumbing Fixtures:  Connect drainage piping in sizes indicated, but not smaller than required by plumbing code.

          - Plumbing Fixtures and Equipment:  Connect atmospheric vent piping in sizes indicated, but not smaller than required by authorities having jurisdiction.

          - Plumbing Specialties:  Connect drainage and vent piping in sizes indicated, but not smaller than required by plumbing code.

          - Install test tees (wall cleanouts) in conductors near floor and floor cleanouts with cover flush with floor.

Pit installation option in first subparagraph below should be detailed on Drawings.

          - Equipment:  Connect drainage piping as indicated.  Provide shutoff valve if indicated and union for each connection.

        - Connect force-main piping to the following:

Revise two subparagraphs below to suit Project.

          - Sanitary Sewer:  To existing force main as indicated.

          - Sewage Pump:  To sewage pump discharge.

        - Where installing piping adjacent to equipment, allow space for service and maintenance of equipment.

        - Make connections according to the following unless otherwise indicated:

          - Install unions, in piping NPS 2 and smaller, adjacent to each valve and at final connection to each piece of equipment.

      - IDENTIFICATION

        - Identify exposed sanitary waste and vent piping.  Comply with requirements for identification specified in Division 22 Section "Identification for Plumbing Piping and Equipment."

      - FIELD QUALITY CONTROL

Portions of testing and inspection requirements in this article are taken from model plumbing codes.  Revise if requirements vary.

        - During installation, notify authorities having jurisdiction at least 24 hours before inspection must be made.  Perform tests specified below in presence of authorities having jurisdiction.

          - Roughing-in Inspection:  Arrange for inspection of piping before concealing or closing-in after roughing-in and before setting fixtures.

          - Final Inspection:  Arrange for final inspection by authorities having jurisdiction to observe tests specified below and to ensure compliance with requirements.

        - Reinspection:  If authorities having jurisdiction find that piping will not pass test or inspection, make required corrections and arrange for reinspection.

        - Reports:  Prepare inspection reports and have them signed by authorities having jurisdiction.

        - Test sanitary drainage and vent piping according to procedures of authorities having jurisdiction or, in absence of published procedures, as follows:

          - Test for leaks and defects in new piping and parts of existing piping that have been altered, extended, or repaired.  If testing is performed in segments, submit separate report for each test, complete with diagram of portion of piping tested.

          - Leave uncovered and unconcealed new, altered, extended, or replaced drainage and vent piping until it has been tested and approved.  Expose work that was covered or concealed before it was tested.

          - Roughing-in Plumbing Test Procedure:  Test drainage and vent piping except outside leaders on completion of roughing-in.  Close openings in piping system and fill with water to point of overflow, but not less than 10-foot head of water.  From 15 minutes before inspection starts to completion of inspection, water level must not drop.  Inspect joints for leaks.

          - Finished Plumbing Test Procedure:  After plumbing fixtures have been set and traps filled with water, test connections and prove they are gastight and watertight.  Plug vent-stack openings on roof and building drains where they leave building.  Introduce air into piping system equal to pressure of 1-inch wg.  Use U-tube or manometer inserted in trap of water closet to measure this pressure.  Air pressure must remain constant without introducing additional air throughout period of inspection.  Inspect plumbing fixture connections for gas and water leaks.

          - Repair leaks and defects with new materials and retest piping, or portion thereof, until satisfactory results are obtained.

          - Prepare reports for tests and required corrective action.

        - Test force-main piping according to procedures of authorities having jurisdiction or, in absence of published procedures, as follows:

          - Leave uncovered and unconcealed new, altered, extended, or replaced force-main piping until it has been tested and approved.  Expose work that was covered or concealed before it was tested.

          - Cap and subject piping to static-water pressure of 50 psig above operating pressure, without exceeding pressure rating of piping system materials.  Isolate test source and allow to stand for four hours.  Leaks and loss in test pressure constitute defects that must be repaired.

          - Repair leaks and defects with new materials and retest piping, or portion thereof, until satisfactory results are obtained.

          - Prepare reports for tests and required corrective action.

      - CLEANING AND PROTECTION

        - Clean interior of piping.  Remove dirt and debris as work progresses.

        - Protect drains during remainder of construction period to avoid clogging with dirt and debris and to prevent damage from traffic and construction work.

        - Place plugs in ends of uncompleted piping at end of day and when work stops.

Consider using other piping or specify protection by shielding or lightweight insulation if piping surface temperatures are expected to exceed 140 deg F (60 deg C).

        - Exposed PVC Piping:  Protect plumbing vents exposed to sunlight with two coats of water-based latex paint.

      - PIPING SCHEDULE

Retain piping applications from this article.  Coordinate with materials specified in Part 2.  Revise to suit Project.

        - Flanges and unions may be used on aboveground pressure piping unless otherwise indicated.

Retain "any of" option in first paragraph below to allow Contractor to retain piping materials from those retained.

        - Aboveground, soil and waste piping NPS 4 and smaller shall be the following:

Retain one or more of first seven subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

          - Solid-wall PVC pipe, PVC socket fittings, and solvent-cemented joints.

          - Dissimilar Pipe-Material Couplings:  Unshielded, nonpressure transition couplings.

Retain "any of" option in first paragraph below to allow Contractor to retain piping materials from those retained.

Retain "any of" option in first paragraph below to allow Contractor to retain piping materials from those retained.

        - Aboveground, vent piping NPS 4 and smaller shall be the following:

Retain one or more of first seven subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

          - Solid-wall PVC pipe, PVC socket fittings, and solvent-cemented joints.

          - Dissimilar Pipe-Material Couplings:  Unshielded, nonpressure transition couplings.

Retain "any of" option in first paragraph below to allow Contractor to retain piping materials from those retained.

Retain "any of" option in first paragraph below to allow Contractor to retain piping materials from those retained.

        - Aboveground sanitary-sewage force mains NPS 1-1/2 and NPS 2 shall be the following:

Retain one or both subparagraphs below.  If more than one type of material and joining method is used, identify various materials on Drawings and show points of transition from one material to another.

          - Hard copper tube, Type L; copper pressure fittings; and soldered joints.

          - PVC schedule 80 with socket fittings.

Retain "any of" option in first paragraph below to allow Contractor to retain piping materials from those retained.

Retain "any of" option in first paragraph below to allow Contractor to retain piping materials from those retained.

END OF SECTION 221316