Copyright 2007 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 221329 - SANITARY SEWERAGE PUMPS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

Packaged,Terminology and descriptions for pumps used in this Section are from HI 1.1-1.2 and HI 3.1-3.5.

          - Packaged, submersible sewage-pump units.

      - SUBMITTALS

First two paragraphs below are defined in Division 01 Section "Submittal Procedures" as "Action Submittals."

        - Product Data:  For each type of product indicated.  Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.

        - Wiring Diagrams:  For power, signal, and control wiring.

Paragraph below is defined in Division 01 Section "Submittal Procedures" as an "Informational Submittal."

        - Operation and Maintenance Data:  For pumps and controls, to include in operation and maintenance manuals.

      - QUALITY ASSURANCE

        - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

        - UL Compliance:  Comply with UL 778 for motor-operated water pumps.

      - DELIVERY, STORAGE, AND HANDLING

        - Retain shipping flange protective covers and protective coatings during storage.

        - Protect bearings and couplings against damage.

        - Comply with pump manufacturer's written rigging instructions for handling.

      - COORDINATION

        - Coordinate sizes and locations of concrete bases with actual equipment provided.

- PRODUCTS

Verify that pump selected has motor feature in first subparagraph below, if either is required, or delete.

      - PACKAGED, SUBMERSIBLE SEWAGE-PUMP UNITS

Units in this article are complete with pumps, basin, piping, and controls.  Units have limited applications and capacities.  Most manufacturers offer only simplex units, but duplex units are available.  Using these units as the only means of discharging sewage is not recommended.

        - Packaged, Submersible, Nonclog, Sewage-Pump Units:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

Retain option in first subparagraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

          - Basis-of-Design Product:  Subject to compliance with requirements, provide product indicated on Drawings or comparable product by one of the following:

            - Goulds Pumps; ITT Corporation.

            - Grundfos Pumps Corp.

            - Liberty Pumps.

            - Little Giant Pump Co.

            - McDonald, A. Y. Mfg. Co.

            - PACO Pumps; Grundfos Pumps Corporation, U.S.A.

            - Pentair Pump Group; Hydromatic Pumps.

            - Pentair Pump Group; Myers.

            - Sta-Rite Industries, Inc.

            - Zoeller Company.

          - Description:  Factory-assembled and -tested, automatic-operation, basin-mounted, sewage-pump unit.

          - Pump Type:  Submersible, end-suction, single-stage, close-coupled, overhung-impeller centrifugal pump as defined in HI 1.1-1.2 and HI 1.3.

          - Pump Casing:  Cast iron.

          - Impeller:  Brass or cast iron; statically and dynamically balanced, non-clog design, and capable of handling 2-inch (50-mm) diameter solids.

          - Motor:  Hermetically sealed, capacitor-start type; with built-in overload protection; lifting eye or lug; and three-conductor, waterproof power cable of length required and with grounding plug and cable-sealing assembly for connection at pump.

Retain first subparagraph below for simplex pump units.

          - Control:  Manufacturer's standard panel for one pump.

Retain first subparagraph below for duplex pump units.

          - Controls:  Automatic, with mechanical- or mercury-float switches and alternator.

          - Pump Discharge Piping:  Factory or field fabricated, PVC.

          - Basin:  Watertight plastic and of size required for pumps, with inlet pipe connection and gastight cover with pump discharge and vent connections.

If Project has more than one type of configuration of packaged sewage- or wastewater-pump unit, delete paragraph below and schedule packaged sewage and wastewater pumps on Drawings.  See sample schedule in Evaluations.

        - Capacities and Characteristics:

          - System Capacity:  21.

          - Number of Pumps:  One.

          - Each Pump:

            - Capacity:  21.

            - Total Dynamic Head:  20.

            - Speed:  1550.

            - Discharge Pipe Size:  1-1/2 inch.

            - Motor Horsepower:  1/2 inch.

            - Electrical Characteristics:

              - Volts:  120.

              - Phases:  Single.

              - Hertz:  60.

          - Alternator Control Required:  No.

          - Basin:

            - Dimensions:  14 inches.

            - Inlet Size:  1-1/2 inches.

            - Bottom to Inlet Centerline:  As furnished.

            - Vent Size:  1-1/2 inches.

      - MOTORS

Default motor characteristics are specified in Division 22 Section "Common Motor Requirements for Plumbing Equipment."

        - Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements for motors specified in Division 22 Section "Common Motor Requirements for Plumbing Equipment."

          - Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

          - Controllers, Electrical Devices, and Wiring:  Comply with requirements for electrical devices and connections specified in Division 26 Sections.

        - Motors for submersible pumps shall be hermetically sealed.

- EXECUTION

      - EARTHWORK

        - Excavation and filling are specified in Division 31 Section "Earth Moving."

      - EXAMINATION

        - Examine roughing-in for plumbing piping to verify actual locations of sanitary drainage and vent piping connections before sewage pump installation.

      - INSTALLATION

        - Pump Installation Standards:

          - Comply with HI 1.4 for installation of centrifugal pumps.

        - Equipment Mounting:  Install sewage pumps using elastomeric pads.

Retain first paragraph below for pumps with wall-mounted controls and coordinate with Drawings.  Delete both if wiring methods for system are indicated on Drawings.

        - Wiring Method:  Comply with requirements in Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

        - Wiring within Enclosures:  Bundle, lace, and train conductors to terminal points with no excess and without exceeding manufacturer's limitations on bending radii.  Provide and use lacing bars and distribution spools.

      - CONNECTIONS

Coordinate pump installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Comply with requirements for piping specified in Division 22 Section "Sanitary Waste and Vent Piping." Drawings indicate general arrangement of piping, fittings, and specialties.

        - Install piping adjacent to equipment to allow service and maintenance.

      - FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments.

        - Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.

Retain first paragraph below to require Contractor to perform tests and inspections.

        - Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

          - Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph below to describe tests and inspections to be performed.

        - Tests and Inspections:

          - Perform each visual and mechanical inspection.

          - Leak Test:  After installation, charge system and test for leaks.  Repair leaks and retest until no leaks exist.

          - Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

          - Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

See Division 01 Section "Quality Requirements" for retesting and reinspecting requirements and Division 01 Section "Execution" for requirements for correcting the Work.

        - Pumps and controls will be considered defective if they do not pass tests and inspections.

        - Prepare test and inspection reports.

      - STARTUP SERVICE

        - Perform startup service.

          - Complete installation and startup checks according to manufacturer's written instructions.

      - ADJUSTING

        - Adjust pumps to function smoothly, and lubricate as recommended by manufacturer.

        - Adjust control set points.

      - DEMONSTRATION

        - Train Owner's maintenance personnel to adjust, operate, and maintain controls and pumps.

END OF SECTION 221329