Copyright 2006 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 233113 - METAL DUCTS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Single-wall rectangular ducts and fittings.

          - Sheet metal materials.

          - Duct liner.

          - Sealants and gaskets.

          - Hangers and supports.

          - Seismic-restraint devices.

      - PERFORMANCE REQUIREMENTS

Retain first paragraph below if Contractor is required to assume responsibility for duct construction design.

        - Delegated Duct Design:  Duct construction, including sheet metal thicknesses, seam and joint construction, reinforcements, and hangers and supports, shall comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" and performance requirements and design criteria indicated in "Duct Schedule" Article.

Retain seismic options and design criteria in first paragraph below that are approved by authorities having jurisdiction.

        - Structural Performance:  Duct hangers and supports and seismic restraints shall withstand the effects of gravity and seismic loads and stresses within limits and under conditions described in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" and SMACNA's "Seismic Restraint Manual:  Guidelines for Mechanical Systems."

Retain one of three subparagraphs below if retaining "SMACNA's 'Seismic Restraint Manual:  Guidelines for Mechanical Systems'" option in paragraph above.  If using other seismic design criteria, delete three subparagraphs below.

          - Seismic Hazard Level C:  Seismic force to weight ratio, 0.15.

Retain paragraph below to comply with LEED-NC Prerequisite EQ 1.

        - Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

      - SUBMITTALS

First three paragraphs below are defined in Division 01 Section "Submittal Procedures" as "Action Submittals."

        - Product Data:  For each type of the following products:

          - Liners and adhesives.

          - Sealants and gaskets.

          - Seismic-restraint devices.

        - Shop Drawings:

          - Fabrication, assembly, and installation, including plans, elevations, sections, components, and attachments to other work.

          - Factory- and shop-fabricated ducts and fittings.

          - Fittings.

          - Reinforcement and spacing.

          - Seam and joint construction.

          - Penetrations through fire-rated and other partitions.

          - Locations for duct accessories, including dampers, turning vanes, and access doors and panels.

          - Hangers and supports, including methods for duct and building attachment, seismic restraints, and vibration isolation.

First paragraph below is defined in Division 01 Section "Submittal Procedures" as a "Delegated-Design Submittal."  Retain with "Performance Requirements" Article if design responsibilities have been delegated to Contractor.

      - QUALITY ASSURANCE

Retain one of first two paragraphs below if welding is required.  If retaining, also retain "Welding certificates" Paragraph in "Submittals" Article.  Retain first paragraph if only one AWS standard is applicable.  Retain second paragraph if more than one AWS standard is referenced.

        - Welding Qualifications:  Qualify procedures and personnel according to AWS D1.1/D1.1M, "Structural Welding Code - Steel," for hangers and supports; AWS D9.1M/D9.1, "Sheet Metal Welding Code," for duct joint and seam welding.

        - Welding Qualifications:  Qualify procedures and personnel according to the following:

Retain applicable subparagraphs below.

          - AWS D1.1/D1.1M, "Structural Welding Code - Steel," for hangers and supports.

          - AWS D1.2/D1.2M, "Structural Welding Code - Aluminum," for aluminum supports.

          - AWS D9.1M/D9.1, "Sheet Metal Welding Code," for duct joint and seam welding.

Retain first two paragraphs below if applying for LEED certification or if requiring compliance with ASHRAE or ASHRAE/IESNA.

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004.

        - ASHRAE Compliance:  Applicable requirements in ASHRAE 62.1-2004, Section 5 - "Systems and Equipment" and Section 7 - "Construction and System Start-Up."

LEED-NC Prerequisite EA 2 requires compliance with requirements in ASHRAE/IESNA 90.1-2004.

        - ASHRAE/IESNA Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004, Section 6.4.4 - "HVAC System Construction and Insulation."

Retain paragraph below for special construction.  Mockups are normally required only for static-pressure classes in excess of 3-inch wg (750 Pa) when verification of maximum allowable leakage is important.  If retaining, indicate location, size, and other details of mockups on Drawings and retain "Leakage Tests" Paragraph in "Field Quality Control" Article.

ASHRAE/IESNA 90.1 requires leakage testing for representative sections totaling no less than 25 percent of installed duct area for ducts designated to operate at a static-pressure class in excess of 3-inch wg (750 Pa).  Consider building a mockup of typical portions of the system that can be tested early in the construction process.  This standard, as enforced by some authorities having jurisdiction, requires duct systems with static-pressure classes in excess of 3-inch wg (750 Pa) to be identified on Drawings.

- PRODUCTS

      - SINGLE-WALL RECTANGULAR DUCTS AND FITTINGS

See "Static-Pressure Classes" and "Leakage and Seal Classes" articles in the Evaluations for discussion on fabrication.

        - General Fabrication Requirements:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" based on indicated static-pressure class unless otherwise indicated.

        - Transverse Joints:  Select joint types and fabricate according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 1-4, "Transverse (Girth) Joints," for static-pressure class, applicable sealing requirements, materials involved, duct-support intervals, and other provisions in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

        - Longitudinal Seams:  Select seam types and fabricate according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 1-5, "Longitudinal Seams - Rectangular Ducts," for static-pressure class, applicable sealing requirements, materials involved, duct-support intervals, and other provisions in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

        - Elbows, Transitions, Offsets, Branch Connections, and Other Duct Construction:  Select types and fabricate according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Chapter 2, "Fittings and Other Construction," for static-pressure class, applicable sealing requirements, materials involved, duct-support intervals, and other provisions in SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

      - SHEET METAL MATERIALS

        - General Material Requirements:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for acceptable materials, material thicknesses, and duct construction methods unless otherwise indicated.  Sheet metal materials shall be free of pitting, seam marks, roller marks, stains, discolorations, and other imperfections.

See "Sheet Metal Materials" Article in the Evaluations for discussion on applicable materials and coatings in first six paragraphs below.

        - Galvanized Sheet Steel:  Comply with ASTM A 653/A 653M.

          - Galvanized Coating Designation:  G60 (Z180).

          - Finishes for Surfaces Exposed to View:  Mill phosphatized.

        - Reinforcement Shapes and Plates:  ASTM A 36/A 36M, steel plates, shapes, and bars; black and galvanized.

          - Where black- and galvanized-steel shapes and plates are used to reinforce aluminum ducts, isolate the different metals with butyl rubber, neoprene, or EPDM gasket materials.

        - Tie Rods:  Galvanized steel, 1/4-inch (6-mm) minimum diameter for lengths 36 inches (900 mm) or less; 3/8-inch (10-mm) minimum diameter for lengths longer than 36 inches (900 mm).

      - DUCT LINER

If the objective of duct liner includes achievement of both thermal performance and sound absorption, then ducts may need additional external insulation to achieve the thermal portion of the objective.  See Division 23 Section "HVAC Insulation" for applicable duct insulation and installation requirements for external duct application.

LEED-NC Prerequisite EA 2 requires that duct insulation R-value comply with ASHRAE/IESNA 90.1-2004 tables titled "Minimum Duct Insulation R-Value, Cooling and Heating Only Supply Ducts and Return Ducts" and "Minimum Duct Insulation R-Value, Combined Heating and Cooling Supply Ducts and Return Ducts."  If using liner alone to satisfy thermal requirements, verify that material selected is available in thickness needed to provide thermal performance without jeopardizing other requirements.

Type I duct liner is available in thicknesses of 1/2 to 2 inches (13 to 50 mm) in 1/2-inch (13-mm) increments; Type II duct liner is available in thicknesses of 1 to 2 inches (25 to 50 mm) in 1/2-inch (13-mm) increments.  Indicate thicknesses on Drawings or in the "Duct Schedule" Article.

When specifying duct liner by referencing ASTM C 1071, specifiers are assured of product qualifications for corrosiveness, water-vapor sorption, fungi resistance, temperature resistance, erosion resistance, odor emission, surface-burning characteristics, apparent thermal conductivity, sound absorption coefficients, bacteria resistance, and combustion characteristics.

        - Fibrous-Glass Duct Liner:  Comply with ASTM C 1071, NFPA 90A, or NFPA 90B; and with NAIMA AH124, "Fibrous Glass Duct Liner Standard."

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

To exceed the minimum requirements set by ASTM C 1071, verify that a particular manufacturer's product can meet the requirements, retain the "Basis-of-Design Product" Subparagraph below, and insert the manufacturer's name and product designation.

          - Basis-of-Design Product:  Subject to compliance with requirements, provide product indicated on Drawings or comparable product by one of the following:

            - CertainTeed Corporation; Insulation Group.

            - Johns Manville.

            - Knauf Insulation.

            - Owens Corning.

Retain first subparagraph below to require thermal conductivity exceeding the minimum requirements in ASTM C 1071.  Retaining subparagraph may create a restrictive proprietary specification.

          - Maximum Thermal Conductivity:

Option for thermal conductivity in first two subparagraphs below exceeds the values in ASTM C 1071.  If retaining, verify availability of performance with duct liner manufacturers.

            - Type I, Flexible:  0.27 Btu x in./h x sq. ft. x deg F (0.039 W/m x K) at 75 deg F (24 deg C) mean temperature.

            - Type II, Rigid:  0.23 Btu x in./h x sq. ft. x deg F (0.033 W/m x K) at 75 deg F (24 deg C) mean temperature.

Antimicrobial coating in first subparagraph below is an optional feature for duct liner.

          - Antimicrobial Erosion-Resistant Coating:  Apply to the surface of the liner that will form the interior surface of the duct to act as a moisture repellent and erosion-resistant coating.  Antimicrobial compound shall be tested for efficacy by an NRTL and registered by the EPA for use in HVAC systems.

          - Water-Based Liner Adhesive:  Comply with NFPA 90A or NFPA 90B and with ASTM C 916.

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

            - For indoor applications, use adhesive that has a VOC content of 80 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Flexible elastomeric duct liner in first paragraph below is not suitable for temperatures higher than 220 deg F (104 deg C).

        - Insulation Pins and Washers:

          - Cupped-Head, Capacitor-Discharge-Weld Pins:  Copper- or zinc-coated steel pin, fully annealed for capacitor-discharge welding, 0.106-inch- (2.6-mm-) diameter shank, length to suit depth of insulation indicated with integral 1-1/2-inch (38-mm) galvanized carbon-steel washer.

          - Insulation-Retaining Washers:  Self-locking washers formed from 0.016-inch- (0.41-mm-) thick galvanized steel; with beveled edge sized as required to hold insulation securely in place but not less than 1-1/2 inches (38 mm) in diameter.

        - Shop Application of Duct Liner:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 2-19, "Flexible Duct Liner Installation."

          - Adhere a single layer of indicated thickness of duct liner with at least 90 percent adhesive coverage at liner contact surface area.  Attaining indicated thickness with multiple layers of duct liner is prohibited.

          - Apply adhesive to transverse edges of liner facing upstream that do not receive metal nosing.

          - Butt transverse joints without gaps, and coat joint with adhesive.

          - Fold and compress liner in corners of rectangular ducts or cut and fit to ensure butted-edge overlapping.

          - Do not apply liner in rectangular ducts with longitudinal joints, except at corners of ducts, unless duct size and dimensions of standard liner make longitudinal joints necessary.

Delete first subparagraph below if air velocities do not exceed 2500 fpm (12.7 m/s).

          - Apply adhesive coating on longitudinal seams in ducts with air velocity of 2500 fpm (12.7 m/s).

Securing method in first subparagraph below is for ducts with air velocities of 2500 fpm (12.7 m/s) and lower.  Use caution when designing lined ducts with air velocities higher than 2500 fpm (12.7 m/s).  See SMACNA for requirements.

          - Secure liner with mechanical fasteners 4 inches (100 mm) from corners and at intervals not exceeding 12 inches (300 mm) transversely; at 3 inches (75 mm) from transverse joints and at intervals not exceeding 18 inches (450 mm) longitudinally.

          - Secure transversely oriented liner edges facing the airstream with metal nosings that have either channel or "Z" profiles or are integrally formed from duct wall.  Fabricate edge facings at the following locations:

            - Fan discharges.

            - Intervals of lined duct preceding unlined duct.

            - Upstream edges of transverse joints in ducts where air velocities are higher than 2500 fpm (12.7 m/s) or where indicated.

Retain first subparagraph below if ducts with air velocities higher than 4000 fpm (20.3 m/s) are anticipated; indicate locations of double-wall ducts on Drawings.  Use solid-metal (unperforated) inner ducts for material-handling exhaust systems.

          - Secure insulation between perforated sheet metal inner duct of same thickness as specified for outer shell.  Use mechanical fasteners that maintain inner duct at uniform distance from outer shell without compressing insulation.

            - Sheet Metal Inner Duct Perforations:  3/32-inch (2.4-mm) diameter, with an overall open area of 23 percent.

          - Terminate inner ducts with buildouts attached to fire-damper sleeves, dampers, turning vane assemblies, or other devices.  Fabricated buildouts (metal hat sections) or other buildout means are optional; when used, secure buildouts to duct walls with bolts, screws, rivets, or welds.

      - SEALANT AND GASKETS

        - General Sealant and Gasket Requirements:  Surface-burning characteristics for sealants and gaskets shall be a maximum flame-spread index of 25 and a maximum smoke-developed index of 50 when tested according to UL 723; certified by an NRTL.

See SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for discussion on seam and joint sealing methods and their applications.  Retain one or more of first three paragraphs below, and identify which sealing system applies to which duct system in the "Duct Schedule" Article.

        - Two-Part Tape Sealing System:

          - Tape:  Woven cotton fiber impregnated with mineral gypsum and modified acrylic/silicone activator to react exothermically with tape to form hard, durable, airtight seal.

          - Tape Width:  3 inches (76 mm).

          - Sealant:  Modified styrene acrylic.

          - Water resistant.

          - Mold and mildew resistant.

          - Maximum Static-Pressure Class:  10-inch wg (2500 Pa), positive and negative.

          - Service:  Indoor and outdoor.

          - Service Temperature:  Minus 40 to plus 200 deg F (Minus 40 to plus 93 deg C).

          - Substrate:  Compatible with galvanized sheet steel (both PVC coated and bare), stainless steel, or aluminum.

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

          - For indoor applications, use sealant that has a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

Retain one of first two paragraphs below.  If retaining second paragraph, verify acceptability with authorities having jurisdiction.

        - Water-Based Joint and Seam Sealant:

          - Application Method:  Brush on.

          - Solids Content:  Minimum 65 percent.

          - Shore A Hardness:  Minimum 20.

          - Water resistant.

          - Mold and mildew resistant.

          - VOC:  Maximum 75 g/L (less water).

          - Maximum Static-Pressure Class:  10-inch wg (2500 Pa), positive and negative.

          - Service:  Indoor or outdoor.

          - Substrate:  Compatible with galvanized sheet steel (both PVC coated and bare), stainless steel, or aluminum sheets.

        - Solvent-Based Joint and Seam Sealant:

          - Application Method:  Brush on.

          - Base:  Synthetic rubber resin.

          - Solvent:  Toluene and heptane.

          - Solids Content:  Minimum 60 percent.

          - Shore A Hardness:  Minimum 60.

          - Water resistant.

          - Mold and mildew resistant.

Retain one of first two subparagraphs below.  Retain first subparagraph if low-emitting materials are required for LEED-NC Credit EQ 4.1.

          - For indoor applications, use sealant that has a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

          - VOC:  Maximum 395 g/L.

          - Maximum Static-Pressure Class:  10-inch wg (2500 Pa), positive or negative.

          - Service:  Indoor or outdoor.

          - Substrate:  Compatible with galvanized sheet steel (both PVC coated and bare), stainless steel, or aluminum sheets.

        - Flanged Joint Sealant:  Comply with ASTM C 920.

          - General:  Single-component, acid-curing, silicone, elastomeric.

          - Type:  S.

          - Grade:  NS.

          - Class:  25.

          - Use:  O.

Retain subparagraph below if low-emitting materials are required for LEED-NC Credit EQ 4.1.

          - For indoor applications, use sealant that has a VOC content of 250 g/L or less when calculated according to 40 CFR 59, Subpart D (EPA Method 24).

        - Flange Gaskets:  Butyl rubber, neoprene, or EPDM polymer with polyisobutylene plasticizer.

O-ring seals are generally available for duct fittings 3 to 24 inches (76 to 610 mm) in diameter.

        - Round Duct Joint O-Ring Seals:

          - Seal shall provide maximum leakage class of 3 cfm/100 sq. ft. at 1-inch wg (0.14 L/s per sq. m at 250 Pa) and shall be rated for 10-inch wg (2500-Pa) static-pressure class, positive or negative.

Retain one or both subparagraphs below.  These are proprietary seals provided on factory-fabricated, round duct fitting joints and constructed with specific dimensions to ensure a proper seal.

          - EPDM O-ring to seal in concave bead in coupling or fitting spigot.

          - Double-lipped, EPDM O-ring seal, mechanically fastened to factory-fabricated couplings and fitting spigots.

      - HANGERS AND SUPPORTS

Indicate the extent of corrosive environment on Drawings.

        - Hanger Rods for Noncorrosive Environments:  Cadmium-plated steel rods and nuts.

        - Strap and Rod Sizes:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Table 4-1 (Table 4-1M), "Rectangular Duct Hangers Minimum Size," and Table 4-2, "Minimum Hanger Sizes for Round Duct."

        - Steel Cables for Galvanized-Steel Ducts:  Galvanized steel complying with ASTM A 603.

        - Steel Cables for Stainless-Steel Ducts:  Stainless steel complying with ASTM A 492.

        - Steel Cable End Connections:  Cadmium-plated steel assemblies with brackets, swivel, and bolts designed for duct hanger service; with an automatic-locking and clamping device.

        - Duct Attachments:  Sheet metal screws, blind rivets, or self-tapping metal screws; compatible with duct materials.

        - Trapeze and Riser Supports:

          - Supports for Galvanized-Steel Ducts:  Galvanized-steel shapes and plates.

      - SEISMIC-RESTRAINT DEVICES

Coordinate specifications for seismic-restraint components in this article with structural engineer and with Drawings.  See the "Seismic Considerations" Article in the Evaluations for discussion on seismic restraints.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain first paragraph and list of manufacturers below.  See Division 01 Section "Product Requirements."

        - Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

          - Cooper B-Line, Inc.; a division of Cooper Industries.

          - Ductmate Industries, Inc.

          - Hilti Corp.

          - Kinetics Noise Control.

          - Loos & Co.; Cableware Division.

          - Mason Industries.

          - TOLCO; a brand of NIBCO INC.

          - Unistrut Corporation; Tyco International, Ltd.

See the Evaluations in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment" for discussion on seismic-restraint capacities and rating services.

        - General Requirements for Restraint Components:  Rated strengths, features, and applications shall be as defined in reports by an agency acceptable to authorities having jurisdiction.

          - Structural Safety Factor:  Allowable strength in tension, shear, and pullout force of components shall be at least four times the maximum seismic forces to which they will be subjected.

        - Channel Support System:  Shop- or field-fabricated support assembly made of slotted steel channels rated in tension, compression, and torsion forces and with accessories for attachment to braced component at one end and to building structure at the other end.  Include matching components and corrosion-resistant coating.

        - Restraint Cables:  ASTM A 603, galvanized-steel cables with end connections made of cadmium-plated steel assemblies with brackets, swivel, and bolts designed for restraining cable service; and with an automatic-locking and clamping device or double-cable clips.

Retain first paragraph below for strengthening resistance of hanger rods against seismic forces that may cause rods to buckle.  Use with either channel- or cable-type bracing assemblies.  Detail fabrication and indicate locations on Drawings.

        - Hanger Rod Stiffener:  Steel tube or steel slotted-support-system sleeve with internally bolted connections to hanger rod.

        - Mechanical Anchor Bolts:  Drilled-in and stud-wedge or female-wedge type.  Select anchor bolts with strength required for anchor and as tested according to ASTM E 488.

- EXECUTION

      - DUCT INSTALLATION

Coordinate duct layout and duct accessory arrangement with Drawings.

        - Drawing plans, schematics, and diagrams indicate general location and arrangement of duct system.  Indicated duct locations, configurations, and arrangements were used to size ducts and calculate friction loss for air-handling equipment sizing and for other design considerations.  Install duct systems as indicated unless deviations to layout are approved on Shop Drawings and Coordination Drawings.

        - Install ducts according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" unless otherwise indicated.

        - Install round ducts in maximum practical lengths.

        - Install ducts with fewest possible joints.

        - Install factory- or shop-fabricated fittings for changes in direction, size, and shape and for branch connections.

        - Unless otherwise indicated, install ducts vertically and horizontally, and parallel and perpendicular to building lines.

        - Install ducts close to walls, overhead construction, columns, and other structural and permanent enclosure elements of building.

        - Install ducts with a clearance of 1 inch (25 mm), plus allowance for insulation thickness.

        - Route ducts to avoid passing through transformer vaults and electrical equipment rooms and enclosures.

        - Where ducts pass through non-fire-rated interior partitions and exterior walls and are exposed to view, cover the opening between the partition and duct or duct insulation with sheet metal flanges of same metal thickness as the duct.  Overlap openings on four sides by at least 1-1/2 inches (38 mm).

        - Where ducts pass through fire-rated interior partitions and exterior walls, install fire dampers.

        - Protect duct interiors from moisture, construction debris and dust, and other foreign materials.  Comply with SMACNA's "Duct Cleanliness for New Construction Guidelines."

      - INSTALLATION OF EXPOSED DUCTWORK

        - Protect ducts exposed in finished spaces from being dented, scratched, or damaged.

        - Trim duct sealants flush with metal.  Create a smooth and uniform exposed bead.  Do not use two-part tape sealing system.

        - Grind welds to provide smooth surface free of burrs, sharp edges, and weld splatter.  When welding stainless steel with a No. 3 or 4 finish, grind the welds flush, polish the exposed welds, and treat the welds to remove discoloration caused by welding.

        - Maintain consistency, symmetry, and uniformity in the arrangement and fabrication of fittings, hangers and supports, duct accessories, and air outlets.

        - Repair or replace damaged sections and finished work that does not comply with these requirements.

      - DUCT SEALING

Retain one of two paragraphs below.  Retain first paragraph if retaining subparagraphs for seal class and leakage class in "Duct Schedule" Article; otherwise, delete first and retain second paragraph.

        - Seal ducts for duct static-pressure, seal classes, and leakage classes specified in "Duct Schedule" Article according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

LEED-NC Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004, in which Section 6.4.4.2.1 - "Duct Sealing" requires a minimum seal class for various duct locations and pressures indicated in paragraph below.

        - Seal ducts to the following seal classes according to SMACNA's "HVAC Duct Construction Standards - Metal and Flexible":

          - Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

          - Unconditioned Space, Exhaust Ducts:  Seal Class C.

          - Unconditioned Space, Return-Air Ducts:  Seal Class B.

          - Conditioned Space, Exhaust Ducts:  Seal Class B.

          - Conditioned Space, Return-Air Ducts:  Seal Class C.

      - HANGER AND SUPPORT INSTALLATION

        - Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Chapter 4, "Hangers and Supports."

Verify attachment selection and spacing in first two paragraphs below with structural engineer.

        - Building Attachments:  Concrete inserts, powder-actuated fasteners, or structural-steel fasteners appropriate for construction materials to which hangers are being attached.

          - Where practical, install concrete inserts before placing concrete.

          - Install powder-actuated concrete fasteners after concrete is placed and completely cured.

          - Use powder-actuated concrete fasteners for standard-weight aggregate concretes or for slabs more than 4 inches (100 mm) thick.

          - Do not use powder-actuated concrete fasteners for lightweight-aggregate concretes or for slabs less than 4 inches (100 mm) thick.

Retain subparagraph below for Projects that require seismic restraints.

          - Do not use powder-actuated concrete fasteners for seismic restraints.

        - Hanger Spacing:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Table 4-1 (Table 4-1M), "Rectangular Duct Hangers Minimum Size," and Table 4-2, "Minimum Hanger Sizes for Round Duct," for maximum hanger spacing; install hangers and supports within 24 inches (610 mm) of each elbow and within 48 inches (1200 mm) of each branch intersection.

        - Hangers Exposed to View:  Threaded rod and angle or channel supports.

        - Support vertical ducts with steel angles or channel secured to the sides of the duct with welds, bolts, sheet metal screws, or blind rivets; support at each floor and at a maximum intervals of 16 feet (5 m).

        - Install upper attachments to structures.  Select and size upper attachments with pull-out, tension, and shear capacities appropriate for supported loads and building materials where used.

      - SEISMIC-RESTRAINT-DEVICE INSTALLATION

        - Install ducts with hangers and braces designed to support the duct and to restrain against seismic forces required by applicable building codes.  Comply with SMACNA's "Seismic Restraint Manual:  Guidelines for Mechanical Systems."

Options for 40 and 80 feet (12 and 24 m) in first subparagraph below are recommended by SMACNA's "Seismic Restraint Manual:  Guidelines for Mechanical Systems."  Revise these dimensions based on the configuration of duct and the seismic hazard.

          - Space lateral supports a maximum of 40 feet (12 m) o.c., and longitudinal supports a maximum of 80 feet (24 m) o.c.

          - Brace a change of direction longer than 12 feet (3.7 m).

        - Select seismic-restraint devices with capacities adequate to carry present and future static and seismic loads.

        - Install cables so they do not bend across edges of adjacent equipment or building structure.

        - Install cable restraints on ducts that are suspended with vibration isolators.

        - Install seismic-restraint devices using methods approved by an agency acceptable to authorities having jurisdiction.

        - Attachment to Structure:  If specific attachment is not indicated, anchor bracing and restraints to structure, to flanges of beams, to upper truss chords of bar joists, or to concrete members.

        - Drilling for and Setting Anchors:

          - Identify position of reinforcing steel and other embedded items prior to drilling holes for anchors.  Do not damage existing reinforcement or embedded items during drilling.  Notify the Architect if reinforcing steel or other embedded items are encountered during drilling.  Locate and avoid prestressed tendons, electrical and telecommunications conduit, and gas lines.

          - Do not drill holes in concrete or masonry until concrete, mortar, or grout has achieved full design strength.

          - Wedge Anchors:  Protect threads from damage during anchor installation.  Heavy-duty sleeve anchors shall be installed with sleeve fully engaged in the structural element to which anchor is to be fastened.

          - Set anchors to manufacturer's recommended torque, using a torque wrench.

          - Install zinc-coated steel anchors for interior applications and stainless-steel anchors for applications exposed to weather.

      - CONNECTIONS

Coordinate duct installations and specialty arrangements with Drawings.

        - Make connections to equipment with flexible connectors complying with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible."

        - Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible" for branch, outlet and inlet, and terminal unit connections.

      - PAINTING

        - Paint interior of metal ducts that are visible through registers and grilles and that do not have duct liner.  Apply one coat of flat, black, latex paint over a compatible galvanized-steel primer.  Paint materials and application requirements are specified in Division 09 painting Sections.

      - FIELD QUALITY CONTROL

        - Perform tests and inspections.

Retain first paragraph below for ducts in pressure classes 3-inch wg (750 Pa) and higher or if applying for LEED credits.  It may not be economically practical to test ducts in pressure classes less than 3-inch wg (750 Pa).

Retain first paragraph below if duct cleaning is required.  Text was taken from NADCA ACR, dated 2005.

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, in which Section 7.2.4 - "Ventilation System Start-Up" requires that distribution systems be clean of dirt and debris.

        - Duct System Cleanliness Tests:

          - Visually inspect duct system to ensure that no visible contaminants are present.

          - Test sections of metal duct system, chosen randomly by Owner, for cleanliness according to "Vacuum Test" in NADCA ACR, "Assessment, Cleaning and Restoration of HVAC Systems."

            - Acceptable Cleanliness Level:  Net weight of debris collected on the filter media shall not exceed 0.75 mg/100 sq. cm.

See Division 01 Section "Quality Requirements" for retesting and reinspecting requirements and Division 01 Section "Execution" for requirements for correcting the Work.

        - Duct system will be considered defective if it does not pass tests and inspections.

        - Prepare test and inspection reports.

      - DUCT CLEANING

Retain this article for applications where construction dust and debris in duct system must be removed before air-system operation, or if applying for LEED certification.

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, in which Section 7.2.4 - "Ventilation System Start-Up" requires that distribution systems be clean of dirt and debris.

        - Clean new duct system(s) before testing, adjusting, and balancing.

        - Use service openings for entry and inspection.

          - Create new openings and install access panels appropriate for duct static-pressure class if required for cleaning access.  Provide insulated panels for insulated or lined duct.  Patch insulation and liner as recommended by duct liner manufacturer.  Comply with Division 23 Section "Air Duct Accessories" for access panels and doors.

          - Disconnect and reconnect flexible ducts as needed for cleaning and inspection.

          - Remove and reinstall ceiling to gain access during the cleaning process.

        - Particulate Collection and Odor Control:

          - When venting vacuuming system inside the building, use HEPA filtration with 99.97 percent collection efficiency for 0.3-micron-size (or larger) particles.

          - When venting vacuuming system to outdoors, use filter to collect debris removed from HVAC system, and locate exhaust downwind and away from air intakes and other points of entry into building.

        - Clean the following components by removing surface contaminants and deposits:

          - Air outlets and inlets (registers, grilles, and diffusers).

          - Return and exhaust fans including fan housings, plenums (except ceiling supply and return plenums), scrolls, blades or vanes, shafts, baffles, dampers, and drive assemblies.

          - Air-handling unit internal surfaces and components including mixing box, coil section, air wash systems, spray eliminators, condensate drain pans, humidifiers and dehumidifiers, filters and filter sections, and condensate collectors and drains.

          - Coils and related components.

          - Return-air ducts, dampers, actuators, and turning vanes except in ceiling plenums and mechanical equipment rooms.

          - Supply-air ducts, dampers, actuators, and turning vanes.

          - Dedicated exhaust and ventilation components and makeup air systems.

        - Mechanical Cleaning Methodology:

          - Clean metal duct systems using mechanical cleaning methods that extract contaminants from within duct systems and remove contaminants from building.

          - Use vacuum-collection devices that are operated continuously during cleaning.  Connect vacuum device to downstream end of duct sections so areas being cleaned are under negative pressure.

          - Use mechanical agitation to dislodge debris adhered to interior duct surfaces without damaging integrity of metal ducts, duct liner, or duct accessories.

          - Clean fibrous-glass duct liner with HEPA vacuuming equipment; do not permit duct liner to get wet.  Replace fibrous-glass duct liner that is damaged, deteriorated, or delaminated or that has friable material, mold, or fungus growth.

          - Clean coils and coil drain pans according to NADCA 1992.  Keep drain pan operational.  Rinse coils with clean water to remove latent residues and cleaning materials; comb and straighten fins.

          - Provide drainage and cleanup for wash-down procedures.

          - Antimicrobial Agents and Coatings:  Apply EPA-registered antimicrobial agents if fungus is present.  Apply antimicrobial agents according to manufacturer's written instructions after removal of surface deposits and debris.

      - START UP

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004;

        - Air Balance:  Comply with requirements in Division 23 Section "Testing, Adjusting, and Balancing for HVAC."

      - DUCT SCHEDULE

        - Fabricate ducts with galvanized sheet steel except as otherwise indicated and as follows:

Retain applicable subparagraphs in this article to set criteria for pressure class, duct seal-class level, and duct-leakage class; or delete applicable subparagraphs and indicate pressure class, duct seal-class level, and duct-leakage class on Drawings.  If retaining duct seal and leakage requirements in this article, retain first paragraph in "Duct Sealing" Article.  Both seal class and leakage class are included in this article and either one can be deleted, or both can remain if they are consistent.

Paragraphs below are examples of broad system classifications.  Revise to suit Project or indicate requirements on Drawings if a more refined classification is required.

See ASHRAE duct leakage recommendations in 2005 ASHRAE HANDBOOK - "Fundamentals," Chapter 35, "Duct Design," Table 7, "Recommended Ductwork Leakage Class by Duct Type."

LEED-NC Prerequisite EA 2 requires compliance with ASHRAE/IESNA 90.1-2004, in which Section 6.4.4.2.1 - "Duct Sealing" requires a minimum seal-class level (A, B, or C) for various duct locations and pressures and specifies seal-class levels for joints and seams in ducts located outdoors, in unconditioned spaces, and in conditioned spaces.  Retain second paragraph in "Duct Sealing" Article if applying for LEED certification and requirements are not defined in this article or on Drawings.

          - Ducts Connected to Equipment Not Listed Above:

            - Pressure Class:  Positive or negative 1-inch wg (250 Pa).

            - Minimum SMACNA Seal Class:  B.

            - SMACNA Leakage Class for Rectangular:  3.

        - Intermediate Reinforcement:

          - Galvanized-Steel Ducts:  Galvanized steel.

        - Liner:

LEED-NC Prerequisite EA 2 requires that duct insulation R-value comply with ASHRAE/IESNA 90.1-2004 tables titled "Minimum Duct Insulation R-Value, Cooling and Heating Only Supply Ducts and Return Ducts" and "Minimum Duct Insulation R-Value, Combined Heating and Cooling Supply Ducts and Return Ducts."  If using liner alone to satisfy thermal requirements, verify that material selected is available in thickness needed to provide thermal performance without jeopardizing other requirements.

Flexible elastomeric insulation is available in thicknesses through 1-1/2 inches (38 mm), which comply with NFPA 90A.  Some options in subparagraphs below may create a restrictive proprietary specification.  Verify availability of performance with manufacturers.

Retain one option for material and one option for thickness, or insert another thickness, in each of six subparagraphs below.

          - Return Air Ducts:  Fibrous glass, Type I, 1 inch (25 mm) thick.

          - Exhaust Air Ducts:  Fibrous glass, Type I, 1 inch (25 mm) thick.

          - Transfer Ducts:  Fibrous glass, Type I, 1 inch (25 mm) thick

LEED-NC Prerequisite EA 2 requires that duct insulation R-value comply with ASHRAE/IESNA 90.1-2004 tables titled "Minimum Duct Insulation R-Value, Cooling and Heating Only Supply Ducts and Return Ducts" and "Minimum Duct Insulation R-Value, Combined Heating and Cooling Supply Ducts and Return Ducts."  If using interstitial insulation alone to satisfy thermal requirements, verify that material selected is available in thickness needed to provide thermal performance without jeopardizing other requirements.

Delete paragraph below if branch fittings are detailed on Drawings.

        - Branch Configuration:

          - Rectangular Duct:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 2-6, "Branch Connections."

            - Rectangular Main to Rectangular Branch:  45-degree entry.

            - Rectangular Main to Round Branch:  Spin in.

          - Round and Flat Oval:  Comply with SMACNA's "HVAC Duct Construction Standards - Metal and Flexible," Figure 3-4, "90 Degree Tees and Laterals," and Figure 3-5, "Conical Tees."  Saddle taps are permitted in existing duct.

            - Velocity 1000 fpm (5 m/s) or Lower:  90-degree tap.

END OF SECTION 233113