Copyright 2008 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238126 - SPLIT-SYSTEM AIR-CONDITIONERS

This Section includes requirements for the LEED Rating System.  However, equipment specified in this Section may not qualify for LEED Rating System prerequisites and credits.  Verify with manufacturers that the requirements for prerequisites and credits can be met.  To achieve prerequisites and obtain credits, HVAC system design alternatives that do not include computer-room air conditioners may be required.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section includes split-system air-conditioning units consisting of separate evaporator-fan and compressor-condenser components.

      - SUBMITTALS

First four paragraphs below are defined in Division 01 Section "Submittal Procedures" as "action submittals."

        - Product Data:  For each type of product indicated.  Include rated capacities, operating characteristics, and furnished specialties and accessories.  Include performance data in terms of capacities, outlet velocities, static pressures, sound power characteristics, motor requirements, and electrical characteristics.

Retain first paragraph below if HCFC-free refrigerants are required for LEED-NC Credit EA 4; coordinate with requirements selected in Part 2 for refrigerants.

      - QUALITY ASSURANCE

        - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

        - ASHRAE Compliance:

          - Fabricate and label refrigeration system to comply with ASHRAE 15, "Safety Standard for Refrigeration Systems."

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004.  In addition to establishing minimum ventilation rates, ASHRAE 62.1-2004 includes requirements for controls, surfaces in contact with the airstream, particulate and gaseous filtration, humidification and dehumidification, drain-pan construction and connection, finned-tube coil selection and cleaning, and equipment access.  See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.  Verify, with manufacturers, availability of units with components and features that comply with these requirements.  ASHRAE 62.1-2007 is now the current version but LEED Version 2.2 explicitly refers to the 2004 edition without amendments.

          - ASHRAE Compliance:  Applicable requirements in ASHRAE 62.1-2004,  Section 4 - "Outdoor Air Quality," Section 5 - "Systems and Equipment," Section 6 - " Procedures," and Section 7 - "Construction and System Start-Up."

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.  See "LEED Rating System" Article in the Evaluations for discussion on this prerequisite.

        - ASHRAE/IESNA Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004.

      - COORDINATION

Retain first paragraph below if remote condensing units are located on grade; retain second paragraph if they are located on roof.

        - Coordinate sizes and locations of concrete bases with actual equipment provided.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork are specified in Division 03 Section "Cast-in-Place Concrete."

        - Coordinate sizes and locations of roof curbs, equipment supports, and roof penetrations with actual equipment provided.

      - WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 01 Section "Product Requirements."

        - Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of split-system air-conditioning units that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2.

          - Warranty Period:

            - For Compressor: Five year(s) from date of Substantial Completion.

            - For Parts: One  year(s) from date of Substantial Completion.

            - For Labor: One year(s) from date of Substantial Completion.

      - EXTRA MATERIALS

        - Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Filters:  One set(s) for each air-handling unit.

          - Gaskets:  One set(s) for each access door.

- PRODUCTS

      - MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

Retain option in paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

        - Basis-of-Design Product:  Subject to compliance with requirements, provide product indicated on Drawings or comparable product by one of the following:

Verify that manufacturers retained in the list below make combination of unit components retained.

          - Carrier Corporation; Home Comfort and HVAC Building & Industrial Systems.

          - Coleman Company Inc. (The).

          - First Operations LP.

          - Friedrich Air Conditioning Company.

          - Koldwave, Inc.; a Mestek company.

          - Lennox International Inc.

          - Mitsubishi Electric & Electronics USA, Inc.; HVAC Advanced Products Division.

          - Mitsubishi Electric Sales Canada Inc.

          - Mitsubishi Heavy Industries America, Inc.

          - SANYO North America Corporation; SANYO Fisher Company.

          - Trane; a business of American Standard companies.

          - YORK; a Johnson Controls company.

      - INDOOR UNITS 5 TONS OR LESS

        - Wall-Mounted, Evaporator-Fan Components:

          - Cabinet:  Enameled steel with removable panels on front and ends in color selected by Architect, and discharge drain pans with drain connection.

          - Refrigerant Coil:  Copper tube, with mechanically bonded aluminum fins and thermal-expansion valve.  Comply with ARI 210/240.

Retain "Electric Coil" Subparagraph below for heat-pump units and supplemental electric heat.

          - Electric Coil:  Helical, nickel-chrome, resistance-wire heating elements; with refractory ceramic support bushings, automatic-reset thermal cutout, built-in magnetic contactors, manual-reset thermal cutout, airflow proving device, and one-time fuses in terminal box for overcurrent protection.

          - Fan:  Direct drive, centrifugal.

          - Fan Motors:

            - Comply with NEMA designation, temperature rating, service factor, enclosure type, and efficiency requirements specified in Division 23 Section "Common Motor Requirements for HVAC Equipment."

            - Multitapped, multispeed with internal thermal protection and permanent lubrication.

Retain first subparagraph below if enclosure is not open-dripproof type.  Retain second subparagraph for premium efficiency.

            - Enclosure Type:  Totally enclosed, fan cooled.

            - NEMA Premium (TM) efficient motors as defined in NEMA MG 1.

            - Controllers, Electrical Devices, and Wiring:  Comply with requirements for electrical devices and connections specified in Division 26 Sections.

Retain first subparagraph below to require that disconnect switches be supplied with unit.

            - Mount unit-mounted disconnect switches on interior of unit.

If unique characteristics are required for motors in this Section, insert subparagraphs below.

Retain first subparagraph below to comply with LEED-NC Prerequisite EQ 1.

          - Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

          - Condensate Drain Pans:

First option in first subparagraph below is minimum slope in ASHRAE 62.1-2004.

            - Fabricated with two percent slope in at least two planes to collect condensate from cooling coils (including coil piping connections, coil headers, and return bends) and humidifiers, and to direct water toward drain connection.

Retain option in first subparagraph below to comply with LEED-NC Prerequisite EQ 1; otherwise, insert distance.

              - Length:  Extend drain pan downstream from leaving face to comply with ASHRAE 62.1-2004.

              - Depth:  A minimum of 1 inch deep.

Retain one of first two subparagraphs below.

            - Single-wall, stainless-steel sheet.

            - Drain Connection:  Located at lowest point of pan and sized to prevent overflow.  Terminate with threaded nipple on both ends of pan.

              - Minimum Connection Size:  NPS 1.

Retain first subparagraph below for galvanized-steel drain pans; delete for stainless-steel drain pans.

            - Pan-Top Surface Coating:  Asphaltic waterproofing compound.

          - Air Filtration Section:

See Evaluations for discussion on filter characteristics and applications.  LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, which requires a MERV rating of 6 or higher.

            - General Requirements for Air Filtration Section:

              - Comply with NFPA 90A.

              - Minimum Arrestance:  According to ASHRAE 52.1 and MERV according to ASHRAE 52.2.

              - Filter-Holding Frames:  Arranged for flat or angular orientation, with access doors on both sides of unit.  Filters shall be removable from one side or lifted out from access plenum.

            - Disposable Panel Filters:

Retain one or more of first seven subparagraphs below, as applicable.  If Project has more than one filter type, indicate filter type for each unit on Drawings.

              - Factory-fabricated, viscous-coated, flat-panel type.

              - Thickness:  1 inch.

              - Arrestance according to ASHRAE 52.1: 80.

              - Merv according to ASHRAE 52.2:  5.

              - Media:  Interlaced glass fibers sprayed with nonflammable adhesive and antimicrobial agent.

              - Frame:  Galvanized steel, with metal grid on outlet side, steel rod grid on inlet side, and hinged; with pull and retaining handles.

      - OUTDOOR UNITS (5 TONS OR LESS)

        - Air-Cooled, Compressor-Condenser Components:

          - Casing:  Steel, finished with baked enamel in color selected by Architect, with removable panels for access to controls, weep holes for water drainage, and mounting holes in base.  Provide brass service valves, fittings, and gage ports on exterior of casing.

          - Compressor:  Hermetically sealed with crankcase heater and mounted on vibration isolation device.  Compressor motor shall have thermal- and current-sensitive overload devices, start capacitor, relay, and contactor.

            - Compressor Type:  Scroll.

Feature in first subparagraph below is not available from all manufacturers.

            - Two-speed compressor motor with manual-reset high-pressure switch and automatic-reset low-pressure switch.

LEED Credit EA 4 awards a single point if all HVAC&R equipment has HCFC-free refrigerants.  R-407C and R-410A are HCFC-free refrigerants.

            - Refrigerant Charge:  R-407C or R-410A.

            - Refrigerant Coil:  Copper tube, with mechanically bonded aluminum fins and liquid subcooler.  Comply with ARI 210/240.

Retain first subparagraph below for heat-pump units.

          - Fan:  Aluminum-propeller type, directly connected to motor.

          - Motor:  Permanently lubricated, with integral thermal-overload protection.

          - Low Ambient Kit:  Permits operation down to 45 deg F (7 deg C).

          - Mounting Base:  Polyethylene.

      - ACCESSORIES

Retain one of first three paragraphs below.  Retain first paragraph if controls are part of overall temperature control system.

        - Control equipment and sequence of operation are specified in Division 23 Sections "Instrumentation and Control for HVAC" and "Sequence of Operations for HVAC Controls."

        - Thermostat:  Wireless infrared functioning to remotely control compressor and evaporator fan, with the following features:

          - Compressor time delay.

          - 24-hour time control of system stop and start.

          - Liquid-crystal display indicating temperature, set-point temperature, time setting, operating mode, and fan speed.

          - Fan-speed selection including auto setting.

        - Automatic-reset timer to prevent rapid cycling of compressor.

        - Refrigerant Line Kits:  Soft-annealed copper suction and liquid lines factory cleaned, dried, pressurized, and sealed; factory-insulated suction line with flared fittings at both ends.

        - Drain Hose:  For condensate.

LEED-NC Credit EA 5 requires continuous metering equipment for monitoring building energy consumption performance over time.  Retain paragraph below if required to comply with requirements for this credit.  Verify availability of control features with unit manufacturers.

        - Additional Monitoring:

          - Monitor constant and variable motor loads.

          - Monitor variable-frequency-drive operation.

          - Monitor economizer cycle.

          - Monitor cooling load.

          - Monitor air distribution static pressure and ventilation air volumes.

      - CAPACITIES AND CHARACTERISTICS

        - Cooling Capacity:  As Scheduled.

        - Indoor Unit: As Scheduled.

        - Outdoor Unit: As Scheduled.

- EXECUTION

      - INSTALLATION

        - Install units level and plumb.

        - Install evaporator-fan components using manufacturer's standard mounting devices securely fastened to building structure.

Retain one of first two paragraphs below for ground-mounted units.

        - Install compressor-condenser components on inside plenum as noted.

        - Support ground-mounted, compressor-condenser components as noted.

Retain first paragraph below if Project is in a seismic area.

        - Install seismic restraints.

        - Install compressor-condenser components on mounting pads as noted.

        - Install and connect precharged refrigerant tubing to component's quick-connect fittings.  Install tubing to allow access to unit.

      - CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Piping installation requirements are specified in other Division 23 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

Retain first subparagraph below for units with hot-water coils.

      - FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments.

        - Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect, test, and adjust components, assemblies, and equipment installations, including connections.

Retain first paragraph below to require Contractor to perform tests and inspections.

        - Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

          - Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph below to describe tests and inspections to be performed.

        - Tests and Inspections:

          - Leak Test:  After installation, charge system and test for leaks.  Repair leaks and retest until no leaks exist.

          - Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

          - Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

        - Remove and replace malfunctioning units and retest as specified above.

        - Prepare test and inspection reports.

      - STARTUP SERVICE

        - Engage a factory-authorized service representative to perform startup service.

          - Complete installation and startup checks according to manufacturer's written instructions.

      - DEMONSTRATION

        - Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain units.

END OF SECTION 238126