Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 260533 - RACEWAY AND BOXES FOR ELECTRICAL SYSTEMS

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - This Section includes raceways, fittings, boxes, enclosures, and cabinets for electrical wiring.

      - DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

        - EMT:  Electrical metallic tubing.

        - ENT:  Electrical nonmetallic tubing.

        - EPDM:  Ethylene-propylene-diene terpolymer rubber.

        - FMC:  Flexible metal conduit.

        - IMC:  Intermediate metal conduit.

        - LFMC:  Liquidtight flexible metal conduit.

        - LFNC:  Liquidtight flexible nonmetallic conduit.

        - NBR:  Acrylonitrile-butadiene rubber.

        - RNC:  Rigid nonmetallic conduit.

      - SUBMITTALS

        - Product Data:  For surface raceways, wireways and fittings, floor boxes, hinged-cover enclosures, and cabinets.

        - Shop Drawings:  For the following raceway components.  Include plans, elevations, sections, details, and attachments to other work.

Retain subparagraph below for custom enclosures only.

          - Custom enclosures and cabinets.

Retain subparagraph and associated subparagraphs below if handholes or boxes for underground wiring are specified; delete if these raceway components are specified in Division 26 Section "Underground Ducts and Raceways for Electrical Systems."

Retain paragraph and subparagraphs below if Drawings do not include detailed conduit routing plans and if Project involves unusual coordination requirements.

        - Coordination Drawings:  Conduit routing plans, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Edit subparagraphs below to suit Project.

          - Structural members in the paths of conduit groups with common supports.

          - HVAC and plumbing items and architectural features in the paths of conduit groups with common supports.

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 26 Section "Vibration and Seismic Controls for Electrical Systems."

Retain first paragraph below if nonconcrete handholes or boxes are specified and testing is specified in Part 2 "Source Quality Control for Underground Enclosures" Article.

        - Qualification Data:  For professional engineer and testing agency.

        - Source quality-control test reports.

      - QUALITY ASSURANCE

        - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

        - Comply with NFPA 70.

- PRODUCTS

      - METAL CONDUIT AND TUBING

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

        - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

          - AFC Cable Systems, Inc.

          - Alflex Inc.

          - Allied Tube & Conduit; a Tyco International Ltd. Co.

          - Anamet Electrical, Inc.; Anaconda Metal Hose.

          - Electri-Flex Co.

          - Manhattan/CDT/Cole-Flex.

          - Maverick Tube Corporation.

          - O-Z Gedney; a unit of General Signal.

          - Wheatland Tube Company.

        - Rigid Steel Conduit:  ANSI C80.1.

Retain first paragraph below for corrosion-resistant power distribution at frequencies above 60 Hz or for other special conditions.

        - EMT:  ANSI C80.3.

In first paragraph below, zinc-coated steel is most common type.  Retain third option to allow Contractor to choose material.

        - FMC:  Zinc-coated steel.

        - Fittings for Conduit (Including all Types and Flexible and Liquidtight), EMT, and Cable:  NEMA FB 1; listed for type and size raceway with which used, and for application and environment in which installed.

Coordinate first subparagraph below with Drawings.

          - Fittings for EMT:  Steel, set-screw type.

Retain paragraph below to require some threaded joints of rigid steel conduit or IMC, or their fittings, to be treated with joint compound for improved conductivity, resistance to oxidation, or ease of assembly and disassembly.

        - Joint Compound for Rigid Steel Conduit:  Listed for use in cable connector assemblies, and compounded for use to lubricate and protect threaded raceway joints from corrosion and enhance their conductivity.

      - NONMETALLIC CONDUIT AND TUBING

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

        - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

          - AFC Cable Systems, Inc.

          - Anamet Electrical, Inc.; Anaconda Metal Hose.

          - Arnco Corporation.

          - CANTEX Inc.

          - CertainTeed Corp.; Pipe & Plastics Group.

          - Condux International, Inc.

          - ElecSYS, Inc.

          - Electri-Flex Co.

          - Lamson & Sessions; Carlon Electrical Products.

          - Manhattan/CDT/Cole-Flex.

          - RACO; a Hubbell Company.

          - Thomas & Betts Corporation.

See Evaluations for descriptions of nonmetallic conduit types.

        - RNC:  NEMA TC 2, Type EPC-40-PVC, unless otherwise indicated.

        - LFNC:  UL 1660.

        - Fittings for ENT and RNC:  NEMA TC 3; match to conduit or tubing type and material.

        - Fittings for LFNC:  UL 514B.

      - METAL WIREWAYS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

        - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

          - Cooper B-Line, Inc.

          - Hoffman.

          - Square D; Schneider Electric.

        - Description:  Sheet metal sized and shaped as indicated, NEMA 250, Type 1, unless otherwise indicated.

        - Fittings and Accessories:  Include couplings, offsets, elbows, expansion joints, adapters, hold-down straps, end caps, and other fittings to match and mate with wireways as required for complete system.

        - Wireway Covers:  Screw-cover type.

        - Finish:  Manufacturer's standard enamel finish.

      - SURFACE RACEWAYS

Insert requirements for finish-coat paint color, if applicable, in first paragraph below.  See Division 09 for optional field-finish coats.

        - Surface Metal Raceways:  Galvanized steel with snap-on covers.  Manufacturer's standard enamel finish in color selected by Architect.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

          - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

            - Thomas & Betts Corporation.

            - Walker Systems, Inc.; Wiremold Company (The).

            - Wiremold Company (The); Electrical Sales Division.

      - BOXES, ENCLOSURES, AND CABINETS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

        - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

          - Cooper Crouse-Hinds; Div. of Cooper Industries, Inc.

          - EGS/Appleton Electric.

          - Erickson Electrical Equipment Company.

          - Hoffman.

          - Hubbell Incorporated; Killark Electric Manufacturing Co. Division.

          - O-Z/Gedney; a unit of General Signal.

          - RACO; a Hubbell Company.

          - Robroy Industries, Inc.; Enclosure Division.

          - Scott Fetzer Co.; Adalet Division.

          - Spring City Electrical Manufacturing Company.

          - Thomas & Betts Corporation.

          - Walker Systems, Inc.; Wiremold Company (The).

          - Woodhead, Daniel Company; Woodhead Industries, Inc. Subsidiary.

        - Sheet Metal Outlet and Device Boxes:  NEMA OS 1.

In first paragraph below, aluminum boxes are suitable for use with steel raceways in most environments.  Type FD is a device box with extra depth.  Many other configurations are available.

        - Cast-Metal Outlet and Device Boxes:  NEMA FB 1, ferrous alloy, Type FD, with gasketed cover.

See Editing Instruction No. 2 in the Evaluations for a discussion of floor boxes.

        - Metal Floor Boxes:  Cast metal, fully adjustable, rectangular.

        - Small Sheet Metal Pull and Junction Boxes:  NEMA OS 1.

Coordinate first paragraph and subparagraphs below with Drawings if hinged cover enclosures other than NEMA 250, Type 1 are required, e.g., very dusty areas, and if consideration should be given to use of NEMA 250, Type 12 enclosures.

        - Cabinets:

          - NEMA 250, Type 1, galvanized-steel box with removable interior panel and removable front, finished inside and out with manufacturer's standard enamel.

          - Hinged door in front cover with flush latch and concealed hinge.

          - Key latch to match panelboards.

          - Metal barriers to separate wiring of different systems and voltage.

- EXECUTION

      - RACEWAY APPLICATION

Retain this Article to specify type of raceway to be installed.  Coordinate with conductor and cable wiring methods specified in Division 26 Section "Low-Voltage Electrical Power Conductors and Cables" and in other Sections in Divisions 26, 27, and 28.  Do not duplicate information indicated on Drawings, required by NFPA 70, or specified in other Sections in Divisions 26, 27, and 28.  Specify exceptions to requirements.  Verify requirements with authorities having jurisdiction to avoid specifying uses not permitted.  See "Writing Guide" Article in the Evaluations for instructions on editing this Article.

Retain subparagraph and associated subparagraphs below to specify types and structural load ratings of handholes and pull boxes.  See Editing Instruction No. 3 in the Evaluations.

        - Comply with the following indoor applications, unless otherwise indicated:

          - Exposed, Not Subject to Physical Damage:  EMT.

          - Exposed, Not Subject to Severe Physical Damage:  EMT.

          - Concealed in Ceilings and Interior Walls and Partitions:  EMT.

          - Connection to Vibrating Equipment (Including Transformers and Hydraulic, Pneumatic, Electric Solenoid, or Motor-Driven Equipment):  FMC, except use LFMC in damp or wet locations.

          - Raceways for Optical Fiber or Communications Cable:  EMT from jacks to above accessible ceilings. Above accessible ceilings J-hooks are acceptable.

          - Raceways for Optical Fiber or Communications Cable Risers in Vertical Shafts:  EMT.

          - Raceways for Concealed General Purpose Distribution of Optical Fiber or Communications Cable:  EMT.

          - Boxes and Enclosures:  NEMA 250, Type 1.

          - Raceway Fittings for Security Wiring: EMT, all locations.

        - Minimum Raceway Size 3/4-inch  trade size for power. Minimum size for communications shall be 1 inch.

        - Raceway Fittings:  Compatible with raceways and suitable for use and location.

          - Rigid Steel Conduit:  Use threaded rigid steel conduit fittings, unless otherwise indicated.

Retain first paragraph below for high-frequency installation.

        - Do not install aluminum conduits in contact with concrete.

      - INSTALLATION

        - Comply with NECA 1 for installation requirements applicable to products specified in Part 2 except where requirements on Drawings or in this Article are stricter.

        - Keep raceways at least 6 inches (150 mm) away from parallel runs of flues and steam or hot-water pipes.  Install horizontal raceway runs above water and steam piping.

        - Complete raceway installation before starting conductor installation.

        - Arrange stub-ups so curved portions of bends are not visible above the finished slab.

First paragraph below is more restrictive than NFPA 70, which permits up to four quarter bends in a conduit run.  Retain below for more conservative design, with less stress being placed on wire being pulled in.

        - Install no more than the equivalent of three 90-degree bends in any conduit run except for communications conduits, for which fewer bends are allowed.

        - Conceal conduit and EMT within finished walls, ceilings, and floors, unless otherwise indicated.

Retain paragraph below to require application of protective joint compound to threads of rigid steel conduit or IMC, and their fittings, where these raceways are installed outdoors or in wet, damp, or corrosive conditions.  This optional requirement exceeds NFPA70 rules.  If retaining, coordinate with Part 2 "Joint Compound for Rigid Steel Conduit or IMC" Paragraph and with Drawings indicating wet, damp, or corrosive indoor locations.

Retain first paragraph below to exceed NFPA 70 requirements.  NFPA 70 requires insulated bushings or other smooth rounded entry provisions for conduit terminations at all locations where conductors are No. 4 AWG and larger, regardless of the environment.

        - Raceway Terminations at Locations Subject to Moisture or Vibration:  Use insulating bushings to protect conductors, including conductors smaller than No. 4 AWG.

        - Install pull wires in empty raceways.  Use polypropylene or monofilament plastic line with not less than 200-lb tensile strength.  Leave at least 12 inches of slack at each end of pull wire.

Paragraph below is applicable for EMT, ENT, FMC, IMC, RMC, RNC, and optical fiber/communications cable raceways.

        - Raceways for Optical Fiber and Communications Cable:  Install raceways, metallic and nonmetallic, rigid and flexible, as follows:

          - 1-Inch Trade Size and Larger:  Install raceways in maximum lengths of 75 feet.

          - Install with a maximum of two 90-degree bends or equivalent for each length of raceway unless Drawings show stricter requirements.  Separate lengths with pull or junction boxes or terminations at distribution frames or cabinets where necessary to comply with these requirements.

Retain paragraph and subparagraphs below if applicable.

        - Install raceway sealing fittings at suitable, approved, and accessible locations and fill them with listed sealing compound.  For concealed raceways, install each fitting in a flush steel box with a blank cover plate having a finish similar to that of adjacent plates or surfaces.  Install raceway sealing fittings at the following points:

          - Where conduits pass from warm to cold locations, such as boundaries of refrigerated spaces.

          - Where otherwise required by NFPA 70.

Retain paragraph and subparagraphs below unless locations for expansion fittings for PVC conduits are indicated on Drawings.  See Evaluations.

Formula in first subparagraph below provides about 15 percent safety factor (extra expansion-contraction capability).

          - Install fitting(s) that provide expansion and contraction for at least 0.00041 inch per foot of length of straight run per deg F of temperature change.

          - Install each expansion-joint fitting with position, mounting, and piston setting selected according to manufacturer's written instructions for conditions at specific location at the time of installation.

Delete option in first paragraph below if Type AC or MC cable is specified in Division 26 Section "Low-Voltage Electrical Power Conductors and Cables" for lighting fixture connection.

        - Flexible Conduit Connections:  Use maximum of 72 inches of flexible conduit for recessed and semirecessed lighting fixtures, equipment subject to vibration, noise transmission, or movement; and for transformers and motors.

          - Use LFMC in damp or wet locations subject to severe physical damage.

          - Use LFMC in damp or wet locations not subject to severe physical damage.

        - Set metal floor boxes level and flush with finished floor surface.

        - Set nonmetallic floor boxes level.  Trim after installation to fit flush with finished floor surface.

      - FIRESTOPPING

        - Apply firestopping to electrical penetrations of fire-rated floor and wall assemblies to restore original fire-resistance rating of assembly.

      - PROTECTION

        - Provide final protection and maintain conditions that ensure coatings, finishes, and cabinets are without damage or deterioration at time of Substantial Completion.

          - Repair damage to galvanized finishes with zinc-rich paint recommended by manufacturer.

END OF SECTION 260533