Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 262416 - PANELBOARDS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Distribution panelboards.

          - Lighting and appliance branch-circuit panelboards.

      - DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

      - ACTION SUBMITTALS

        - Product Data:  For each type of panelboard, switching and overcurrent protective device, transient voltage suppression device, accessory, and component indicated.  Include dimensions and manufacturers' technical data on features, performance, electrical characteristics, ratings, and finishes.

      - INFORMATIONAL SUBMITTALS

Coordinate first paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as supplemented in "Quality Assurance" Article.

        - Qualification Data:  For qualified testing agency.

Retain first paragraph below if required by seismic criteria applicable to Project.  Coordinate with Section 260548.16 "Seismic Controls for Electrical Systems." See SEI/ASCE 7 for certification requirements for equipment and components.

Retain first paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field Quality-Control Reports:

          - Test procedures used.

          - Test results that comply with requirements.

          - Results of failed tests and corrective action taken to achieve test results that comply with requirements.

Retain option in paragraph below if retaining "Load Balancing" Paragraph in "Adjusting" Article.

        - Panelboard Schedules:  For installation in panelboards.  Submit final versions after load balancing.

      - CLOSEOUT SUBMITTALS

        - Operation and Maintenance Data:  For panelboards and components to include in emergency, operation, and maintenance manuals.  In addition to items specified in Section 017823 "Operation and Maintenance Data," include the following:

          - Manufacturer's written instructions for testing and adjusting overcurrent protective devices.

      - MAINTENANCE MATERIAL SUBMITTALS

Revise this article to include extra materials that Owner may require, such as GFCI or GFEP circuit breakers or circuit breakers used for switching service, which may fail more frequently due to continuous use.

Coordinate with Section 262813 "Fuses" for quantities of spare fuses and spare-fuse cabinet to be provided.

        - Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Keys:  Two spares for each type of panelboard cabinet lock.

          - Fuses for Fused Switches:  Equal to 10 percent of quantity installed for each size and type, but no fewer than three of each size and type.

      - QUALITY ASSURANCE

Retain first paragraph below if Contractor selects testing agency or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article.  Qualification requirements are in addition to those specified in Section 014000 "Quality Requirements," which also includes the definition for "NRTL" (nationally recognized testing laboratory).

        - Testing Agency Qualifications:  Member company of NETA or an NRTL.

          - Testing Agency's Field Supervisor:  Currently certified by NETA to supervise on-site testing.

        - Source Limitations:  Obtain panelboards, overcurrent protective devices, components, and accessories from single source from single manufacturer.

Retain first paragraph below to allow drawing details based on one manufacturer's product to establish requirements and still allow competition.  Coordinate with Section 016000 "Product Requirements."."

        - Product Selection for Restricted Space:  Drawings indicate maximum dimensions for panelboards including clearances between panelboards and adjacent surfaces and other items.  Comply with indicated maximum dimensions.

        - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

        - Comply with NEMA PB 1.

        - Comply with NFPA 70.

      - DELIVERY, STORAGE, AND HANDLING

See "Testing and Inspecting" Article in the Evaluations for guidance on which option to select in paragraph below.

        - Handle and prepare panelboards for installation according to NEMA PB 1.

      - PROJECT CONDITIONS

Retain first paragraph below for panelboards installed in typical environmental conditions.  For panelboards installed outdoors, in unconditioned spaces, or in unusual environmental conditions, revise paragraph to indicate maximum ambient temperature and expected humidity range.  See Editing Instruction No. 2 in the Evaluations.

        - Environmental Limitations:

          - Rate equipment for continuous operation under the following conditions unless otherwise indicated:

            - Ambient Temperature:  Not exceeding minus 22 deg F (minus 30 deg C) to plus 104 deg F (plus 40 deg C).

            - Altitude:  Not exceeding 6600 feet (2000 m).

In first subparagraph below, select first option for panelboards with fused switches; select second option for panelboards with circuit breakers.

Retain first paragraph below or revise to accommodate unusual service conditions that cannot be eliminated.  See Editing Instructions No. 2 and No. 3 in the Evaluations.

        - Service Conditions:  NEMA PB 1, usual service conditions, as follows:

          - Ambient temperatures within limits specified.

          - Altitude not exceeding 6600 feet (2000 m).

Retain paragraph below if interruption of existing electric service is required.

        - Interruption of Existing Electric Service:  Do not interrupt electric service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary electric service according to requirements indicated:

          - Notify Owner no fewer than two days in advance of proposed interruption of electric service.

          - Do not proceed with interruption of electric service without Owner's written permission.

          - Comply with NFPA 70E.

      - COORDINATION

Revise first paragraph below for types of equipment that affect panelboard installation.

        - Coordinate layout and installation of panelboards and components with other construction that penetrates walls or is supported by them, including electrical and other types of equipment, raceways, piping, encumbrances to workspace clearance requirements, and adjacent surfaces.  Maintain required workspace clearances and required clearances for equipment access doors and panels.

Retain paragraph below if freestanding panelboards are specified.

        - Coordinate sizes and locations of concrete bases with actual equipment provided.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified with concrete.

      - WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

        - Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace transient voltage suppression devices that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods with manufacturers listed in Part 2 articles.

          - Warranty Period:  Five years from date of Substantial Completion.

- PRODUCTS

      - GENERAL REQUIREMENTS FOR PANELBOARDS

Retain first paragraph below for projects in seismic areas.  Coordinate with "Informational Submittals" Article for submittal of manufacturer's seismic qualification certification.

        - Fabricate and test panelboards according to IEEE 344 to withstand seismic forces defined in Section 260548.16 "Seismic Controls for Electrical Systems."

        - Enclosures:  Surface-mounted cabinets.

          - Rated for environmental conditions at installed location.

See "Enclosures" Article in the Evaluations for discussion of enclosure types.  Coordinate first five subparagraphs below with Drawings (by identifying the designated areas) or schedules (by including the required enclosure type).  Availability of some enclosure types are limited by a panelboard's ampacity rating, included devices, or physical size; consult manufacturers for availability of, and limitations on, other than Type 1 enclosures.

            - Indoor Dry and Clean Locations:  NEMA 250, Type 1.

Select first option in first subparagraph below for areas subject to lighter levels of contaminants and second option for areas subject to heavier levels.

Retain one of first two subparagraphs below.

          - Hinged Front Cover:  Entire front trim hinged to box and with standard door within hinged trim cover.

First two subparagraphs below are optional features.  Coordinate with Drawings.

          - Skirt for Surface-Mounted Panelboards:  Same gage and finish as panelboard front with flanges for attachment to panelboard, wall, and ceiling or floor.

          - Gutter Extension and Barrier:  Same gage and finish as panelboard enclosure; integral with enclosure body.  Arrange to isolate individual panel sections.

Coordinate first subparagraph below with "Enclosures" Paragraph above.  Back boxes are also available painted.  Revise if required to include special finishes to match, e.g., stainless steel, epoxy, and fiberglass-reinforced polyester.

          - Finishes:

            - Panels and Trim:  Steel, factory finished immediately after cleaning and pretreating with manufacturer's standard two-coat, baked-on finish consisting of prime coat and thermosetting topcoat.

            - Back Boxes:  Galvanized steel.

Retain first subparagraph below for installations in humid tropical environments.

Retain first subparagraph below for use with lighting and appliance branch-circuit and distribution panelboards with doors.  With the increasing use of computer-generated directories, metal frames are becoming an expensive option for most manufacturers.

          - Directory Card:  Inside panelboard door, mounted in transparent card holder.

Retain first paragraph below, and coordinate with Drawings and schedules, if Project requirements include identifying specific entry locations for incoming service or feeder raceways.

        - Incoming Mains Location:  Top or bottom.

        - Phase, Neutral, and Ground Buses:

In first subparagraph below, first option is standard with most manufacturers; second option costs more.

          - Material:  Hard-drawn copper, 98 percent conductivity.

Five subparagraphs below are optional features.  Ground and neutral buses in lighting and appliance panelboards are also referred to as "bars" in manufacturers' literature.  Coordinate with Drawings.

          - Equipment Ground Bus:  Adequate for feeder and branch-circuit equipment grounding conductors; bonded to box.

Isolated ground bus in first subparagraph below is sometimes physically located above and attached to the equipment ground bus with standoff insulators.  Frequently and incorrectly, contractors connect equipment grounding conductors to this bus instead of to the equipment ground bus, which can be hazardous if separate equipment grounding and isolated ground conductors are not both included in the feeder serving the panelboard.

          - Extra-Capacity Neutral Bus:  Neutral bus rated 200 percent of phase bus and UL listed as suitable for nonlinear loads.

Include instructions in first paragraph below if special sizing or oversizing of lugs is required, if allowing optional use of aluminum for circuits sized for copper conductors, or when upsizing conductors for voltage drop.

        - Conductor Connectors:  Suitable for use with conductor material and sizes.

          - Material:  Hard-drawn copper, 98 percent conductivity.

          - Main and Neutral Lugs:  Mechanical type.

See Editing Instruction No. 4 in the Evaluations for guidance on using compression versus mechanical lugs in first four subparagraphs below.

          - Ground Lugs and Bus-Configured Terminators:  Mechanical type.

First three subparagraphs below are optional features.

In first subparagraph below, NEMA PB 1 allows subfeed lugs to be located on the load or line side of main devices or on main-lugs-only panelboards; however, coordinate with specific manufacturers as some have restrictions on which options are available.

          - Gutter-Tap Lugs:  Mechanical type suitable for use with conductor material.  Locate at same end of bus as incoming lugs or main device.

          - Extra-Capacity Neutral Lugs:  Rated 200 percent of phase lugs mounted on extra-capacity neutral bus.

Retain first paragraph below for panelboards that incorporate one or more main service disconnecting and overcurrent protective devices and that are used as the service entrance, outside feeder, or separately derived source means of disconnect and overcurrent protection.

        - Service Equipment Label:  NRTL labeled for use as service equipment for panelboards or load centers with one or more main service disconnecting and overcurrent protective devices.

Retain first paragraph below if future provisions are required.

        - Future Devices:  Mounting brackets, bus connections, filler plates, and necessary appurtenances required for future installation of devices.

Retain one or both paragraphs below for series-rated system or system that has panelboards and circuit breakers rated for full value of short-circuit current available at location of equipment.

        - Panelboard Short-Circuit Current Rating:  Fully rated to interrupt symmetrical short-circuit current available at terminals. No series ratings allowed.

Retain "Surge Suppression" Paragraph below unless field-mounted SPDs are used.  Retain "Type 1" option for service equipment where the device is installed ahead of the service disconnect.  Retain "Type 2" option for panelboards on the load side of the service disconnect.  Field-mounted SPDs are specified in Section 264313 "Surge Protection for Low-Voltage Electrical Power Circuits."

      - LIGHTING AND APPLIANCE BRANCH-CIRCUIT PANELBOARDS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Section 016000 "Product Requirements."

        - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

          - Eaton Electrical Inc.; Cutler-Hammer Business Unit.

          - General Electric Company; GE Consumer & Industrial - Electrical Distribution.

          - Siemens Energy & Automation, Inc.

          - Square D; a brand of Schneider Electric.

        - Panelboards:  NEMA PB 1, lighting and appliance branch-circuit type.

Retain first paragraph below if mains are not indicated on Drawings.

        - Mains:  Lugs only.

        - Branch Overcurrent Protective Devices:  Bolt-on circuit breakers, replaceable without disturbing adjacent units.

Contactors can be incorporated to switch the entire panelboard or only a portion of the circuits.  Coordinate with Drawings and schedules to indicate contactor connections, type, quantity of circuits controlled, current ratings, external control circuits, and number of poles.  Consult manufacturers for their respective limitations on and availability of short-circuit ratings and electrically held contactors, which may not be available from all manufacturers.

        - Doors:  Concealed hinges; secured with flush latch with tumbler lock; keyed alike.

      - DISCONNECTING AND OVERCURRENT PROTECTIVE DEVICES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers.  Retain one of first two paragraphs and list of manufacturers below.  See Section 016000 "Product Requirements."

        - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Retain option in first paragraph below if manufacturer's name and model number are indicated in schedules or plans on Drawings; delete option and insert manufacturer's name and model number if not included on Drawings.

          - Eaton Electrical Inc.; Cutler-Hammer Business Unit.

          - General Electric Company; GE Consumer & Industrial - Electrical Distribution.

          - Siemens Energy & Automation, Inc.

          - Square D; a brand of Schneider Electric.

Coordinate two paragraphs below with Drawings.  See the "Disconnecting and Overcurrent Protective Devices" Article in the Evaluations for guidance on making selections.

Some manufacturers offer shunt-trip operators for their fused switches; however, most do not recommend using this feature for providing ground-fault protection on switches rated 1000 A and above in panelboards; they recommend using MCCBs or switches specified in Section 262413 "Switchboards." Consult manufacturers for availability and limitations if this feature is required.

        - Fused Switch:  NEMA KS 1, Type HD; clips to accommodate specified fuses; lockable handle.

          - Fuses, and Spare-Fuse Cabinet:  Comply with requirements specified in Section 262813 "Fuses."

          - Fused Switch Features and Accessories:  Standard ampere ratings and number of poles.

Accessories and options, in addition to the one in subparagraph below, may be available for some ratings and from some listed manufacturers.  Consult manufacturers for availabilities and unique characteristics.

          - Auxiliary Contacts:  One normally open and normally closed contact(s) that operate with switch handle operation.

        - Non-Fused Switch: Type HD; amperage as indicated on drawings.

      - ACCESSORY COMPONENTS AND FEATURES

Retain this article for overcurrent protective devices that require items in paragraphs below; delete if these items are specified elsewhere, such as in Section 262413 "Switchboards."

        - Accessory Set:  Include tools and miscellaneous items required for overcurrent protective device test, inspection, maintenance, and operation.

Retain paragraph below for circuit breakers with solid-state trip devices.

- EXECUTION

      - EXAMINATION

Referenced NECA and NEMA standards in first paragraph below include similar requirements.  See "Testing and Inspecting" Article in the Evaluations.

        - Receive, inspect, handle, and store panelboards according to NEMA PB 1.1.

        - Examine panelboards before installation.  Reject panelboards that are damaged or rusted or have been subjected to water saturation.

        - Examine elements and surfaces to receive panelboards for compliance with installation tolerances and other conditions affecting performance of the Work.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

Referenced NECA and NEMA standards in first paragraph below include similar requirements.  See "Testing and Inspecting" Article in the Evaluations.

        - Install panelboards and accessories according to NEMA PB 1.1.

        - Mount top of trim 72 inches above finished floor unless otherwise indicated.

Retain first paragraph below for floor-mounted distribution panelboards.  Even if floor mounted, all panelboard cabinets must still be securely attached to a vertical wall or surface.

Retain first paragraph below for large floor-mounted distribution panelboards.

Retain first paragraph below if seismic controls are required for Project.  Coordinate with Drawings.

Ensure that, whatever height is selected for top of trim in first paragraph below, the operating handle of top-most switch or circuit breaker, in on position, is not higher than 79 inches (2000 mm)

        - Mount panelboard cabinet plumb and rigid without distortion of box.

        - Install overcurrent protective devices and controllers not already factory installed.

Subparagraph below assumes that settings are indicated on Drawings or a coordination report is available for Contractor to use.

        - Install filler plates in unused spaces.

Retain first paragraph below if ceilings are accessible or there are raised floors, or when panelboards are located in spaces that will be finished.

        - Stub four 1-inch (27-GRC) empty conduits from panelboard into accessible ceiling space or space designated to be ceiling space in the future.

Retain option in first paragraph below if retaining "Load Balancing" Paragraph in "Adjusting" Article.

        - Arrange conductors in gutters into groups and bundle and wrap with wire ties after completing load balancing.

        - Comply with NECA 1.

      - IDENTIFICATION

        - Identify field-installed conductors, interconnecting wiring, and components.

Retain option in first paragraph below if retaining "Load Balancing" Paragraph in "Adjusting" Article.

        - Create a directory to indicate installed circuit loads after balancing panelboard loads; incorporate Owner's final room designations.  Obtain approval before installing.  Use a computer or typewriter to create directory; handwritten directories are not acceptable.

        - Panelboard Nameplates:  Label each panelboard with a nameplate and where it is fed from.

Retain paragraph below if nameplates are required for individual overcurrent devices in distribution panelboards.

        - Label all receptacle faceplates with panelboard and circuit number.

      - FIELD QUALITY CONTROL

Retain one of first three paragraphs below to identify who shall perform tests and inspections.  If retaining second option in first paragraph, or if retaining second or third paragraph, retain "Field Quality-Control Reports" Paragraph in "Informational Submittals" Article.

Retain first paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments, especially if panelboards include zone-selective interlocking.

Retain first paragraph below to require Contractor to perform tests and inspections.

Retain first two paragraphs below to describe tests and inspections to be performed.

        - Acceptance Testing Preparation:

          - Test insulation resistance for each panelboard bus, component, connecting supply, feeder, and control circuit.

          - Test continuity of each circuit.

        - Tests and Inspections:

          - Perform each visual and mechanical inspection and electrical test stated in NETA Acceptance Testing Specification.  Certify compliance with test parameters.

          - Correct malfunctioning units on-site, where possible, and retest to demonstrate compliance; otherwise, replace with new units and retest.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Panelboards will be considered defective if they do not pass tests and inspections.

Retain paragraph below if tests and inspections are performed by Contractor or manufacturer's field-service representative engaged by Contractor.

        - Prepare test and inspection reports, including a certified report that identifies panelboards included and that describes scanning results.  Include notation of deficiencies detected, remedial action taken, and observations after remedial action.

      - ADJUSTING

        - Adjust moving parts and operable component to function smoothly, and lubricate as recommended by manufacturer.

Select first option in first paragraph below if settings are included in the Contract Documents; select second option if indicated Section is included in the Contract Documents.

Circuit changes made during load balancing may negate color-coding of phases and circuits.  If load balancing proves undesirable or is to be performed by others, delete paragraph below.

        - Load Balancing:  After Substantial Completion, but not more than 60 days after Final Acceptance, measure load balancing and make circuit changes.

          - Measure as directed during period of normal system loading.

          - Perform load-balancing circuit changes outside normal occupancy/working schedule of the facility and at time directed.  Avoid disrupting critical 24-hour services such as fax machines and on-line data processing, computing, transmitting, and receiving equipment.

          - After circuit changes, recheck loads during normal load period.  Record all load readings before and after changes and submit test records.

          - Tolerance:  Difference exceeding 20 percent between phase loads, within a panelboard, is not acceptable.  Rebalance and recheck as necessary to meet this minimum requirement.

END OF SECTION 262416