Copyright 2004 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 262726 - WIRING DEVICES

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - This Section includes the following:

          - Receptacles, receptacles with integral GFCI, and associated device plates.

          - Receptacles with integral surge suppression units.

          - Wall-box motion sensors.

          - Isolated-ground receptacles.

          - Hospital-grade receptacles.

          - Snap switches and wall-box dimmers.

          - Solid-state fan speed controls.

          - Wall-switch and exterior occupancy sensors.

          - Communications outlets.

          - Pendant cord-connector devices.

          - Cord and plug sets.

          - Floor service outlets, poke-through assemblies, service poles, and multioutlet assemblies.

      - DEFINITIONS

Retain term and abbreviations that remain after this Section has been edited.

        - EMI:  Electromagnetic interference.

        - GFCI:  Ground-fault circuit interrupter.

        - Pigtail:  Short lead used to connect a device to a branch-circuit conductor.

        - RFI:  Radio-frequency interference.

        - TVSS:  Transient voltage surge suppressor.

        - UTP:  Unshielded twisted pair.

      - SUBMITTALS

        - Product Data:  For each type of product indicated.

Retain first paragraph below if products have critical features needing hands-on appraisal.

        - Field quality-control test reports.

        - Operation and Maintenance Data:  For wiring devices to include in all manufacturers' packing label warnings and instruction manuals that include labeling conditions.

      - QUALITY ASSURANCE

        - Source Limitations:  Obtain each type of wiring device and associated wall plate through one source from a single manufacturer.  Insofar as they are available, obtain all wiring devices and associated wall plates from a single manufacturer and one source.

        - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

        - Comply with NFPA 70.

      - COORDINATION

Retain this Article if receptacles for Owner-furnished equipment with plugs have unknown or special configurations.

        - Receptacles for Owner-Furnished Equipment:  Match plug configurations.

Retain subparagraph below if cord and plug sets are specified in Part 2.

          - Cord and Plug Sets:  Match equipment requirements.

      - EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

        - Furnish extra materials described in subparagraphs below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Service/Power Poles: One for every 10, but no fewer than one.

          - Floor Service Outlet Assemblies:  One for every 10, but no fewer than one.

          - Poke-Through, Fire-Rated Closure Plugs: One for every five floor service outlets installed, but no fewer than two.

- PRODUCTS

      - MANUFACTURERS

        - Manufacturers' Names:  Shortened versions (shown in parentheses) of the following manufacturers' names are used in other Part 2 articles:

Manufacturers listed below produce an extensive line of nationally distributed wiring devices.  Add manufacturers if desired.

          - Cooper Wiring Devices; a division of Cooper Industries, Inc. (Cooper).

          - Hubbell Incorporated; Wiring Device-Kellems (Hubbell).

          - Leviton Mfg. Company Inc. (Leviton).

          - Pass & Seymour/Legrand; Wiring Devices & Accessories (Pass & Seymour).

      - STRAIGHT BLADE RECEPTACLES

        - Convenience Receptacles, 125 V, 20 A:  Comply with NEMA WD 1, NEMA WD 6 configuration 5-20R, and UL 498.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements, provide one of the following:

Catalog numbers in subparagraphs below are for 20-A devices; revise catalog numbers if 15-A devices are desired.

            - Cooper; 5351 (single), 5352 (duplex).

            - Hubbell; HBL5351 (single), CR5352 (duplex).

            - Leviton; 5891 (single), 5352 (duplex).

            - Pass & Seymour; 5381 (single), 5352 (duplex).

Isolated-ground receptacles are available in a variety of configurations and ratings including locking-blade types up to 50 A and 250 V.  Revise first paragraph and subparagraphs below to suit Project; indicate different types on Drawings.

      - GFCI RECEPTACLES

Non-feed-through-type GFCI unit may be selected where no protection of downstream receptacles is required.

        - General Description:  Straight blade, feed-through type.  Comply with NEMA WD 1, NEMA WD 6, UL 498, and UL 943, Class A, and include indicator light that is lighted when device is tripped.

        - Duplex GFCI Convenience Receptacles, 125 V, 20 A:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements, provide one of the following:

Catalog numbers in subparagraphs below are for feed-through types, arranged to protect receptacles downstream on the same circuit; revise catalog numbers if non-feed-through types are required.

            - Cooper; GF20.

            - Pass & Seymour; 2084.

      - PENDANT CORD-CONNECTOR DEVICES

Revise NEMA configuration in paragraph below to suit Project.  Delete "External Cable Grip" Subparagraph if not required.

        - Description:  Matching, locking-type plug and receptacle body connector; NEMA WD 6 configurations L5-20P and L5-20R, heavy-duty grade.

          - Body:  Nylon with screw-open cable-gripping jaws and provision for attaching external cable grip.

          - External Cable Grip:  Woven wire-mesh type made of high-strength galvanized-steel wire strand, matched to cable diameter, and with attachment provision designed for corresponding connector.

      - CORD AND PLUG SETS

Retain this Article if cord and plug sets for equipment are furnished by Owner or are specified in other Sections.  Coordinate with other Sections and with Part 3.

        - Description:  Match voltage and current ratings and number of conductors to requirements of equipment being connected.

          - Cord:  Rubber-insulated, stranded-copper conductors, with Type SOW-A jacket; with green-insulated grounding conductor and equipment-rating ampacity plus a minimum of 30 percent.

          - Plug:  Nylon body and integral cable-clamping jaws.  Match cord and receptacle type for connection.

      - SNAP SWITCHES

        - Comply with NEMA WD 1 and UL 20.

        - Switches, 120/277 V, 20 A:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements, provide one of the following:

Catalog numbers in subparagraphs below are for 20-A devices; revise catalog numbers if 15-A devices are desired.

            - Cooper; 2221 (single pole), 2222 (two pole), 2223 (three way), 2224 (four way).

            - Hubbell; CS1221 (single pole), CS1222 (two pole), CS1223 (three way), CS1224 (four way).

            - Leviton; 1221-2 (single pole), 1222-2 (two pole), 1223-2 (three way), 1224-2 (four way).

            - Pass & Seymour; 20AC1 (single pole), 20AC2 (two pole), 20AC3 (three way), 20AC4 (four way).

Retain one of first two paragraphs and associated subparagraphs below for square and near-square rectangular rooms.

      - COMMUNICATIONS OUTLETS

        - Voice and Data Outlets:

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two subparagraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

          - Products:  Subject to compliance with requirements, provide one of the following:

            - Cooper; 3560-6.

            - Leviton; 40649.

          - Description:  Double RJ-45, unless noted otherwise, jack for terminating 100-ohm, balanced, four-pair UTP; TIA/EIA-568-B.1; complying with Category 5e.  Comply with UL 1863.

      - WALL PLATES

        - Single and combination types to match corresponding wiring devices.

          - Plate-Securing Screws:  Metal with head color to match plate finish.

          - Material for Finished Spaces:  Smooth, high-impact thermoplastic.

          - Material for Unfinished Spaces:  Galvanized steel.

      - FLOOR SERVICE FITTINGS

Service fittings in first paragraph below are available for voice and data communication cabling as well as for power.  Edit to suit Project.

        - Type:  Modular, pedestal, dual-service units suitable for wiring method used.

        - Compartments:  Barrier separates power from voice and data communication cabling.

        - Power Receptacle:  NEMA WD 6 configuration 5-20R, unless otherwise indicated.

        - Voice and Data Communication Outlets:  Two modular, keyed, color-coded, RJ-45 Category 5e jacks for UTP cable, unless noted otherwise.

      - POKE-THROUGH ASSEMBLIES

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first two paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

        - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

          - Hubbell Incorporated; Wiring Device-Kellems.

          - Pass & Seymour/Legrand; Wiring Devices & Accessories.

          - Square D/ Schneider Electric.

          - Thomas & Betts Corporation.

          - Wiremold Company (The).

        - Description:  Factory-fabricated and -wired assembly of below-floor junction box with multichanneled, through-floor raceway/firestop unit and detachable matching floor service outlet assembly.

Coordinate subparagraph below with Division 27 Section "Communications Horizontal Cabling."

          - Service Outlet Assembly:  Flush type with two simplex receptacles and space for two RJ-45 jacks.

Larger diameter assembly in subparagraph below is available for four simplex receptacles and four voice and data communication outlets in a single, flush-type service outlet.

          - Size:  Selected to fit nominal 4-inch cored holes in floor and matched to floor thickness.

Revise first subparagraph below to coordinate with fire ratings.

          - Fire Rating:  Unit is listed and labeled for fire rating of floor-ceiling assembly.

          - Closure Plug:  Arranged to close unused 4-inch cored openings and reestablish fire rating of floor.

Coordinate subparagraph below with Division 27 Section "Communications Horizontal Cabling."

          - Wiring Raceways and Compartments:  For a minimum of four No. 12 AWG conductors and a minimum of four, 4-pair, Category 5e voice and data communication cables.

      - SERVICE POLES

        - Description:  Factory-assembled and -wired units to extend power and voice and data communication from distribution wiring concealed in ceiling to devices or outlets in pole near floor.

          - Poles:  Nominal 2.5-inch- square cross section, with height adequate to extend from floor to at least 6 inches above ceiling, and with separate channels for power wiring and voice and data communication cabling.

          - Mounting:  Ceiling trim flange with concealed bracing arranged for positive connection to ceiling supports; with pole foot and carpet pad attachment.

Specify final finish in first subparagraph below if known.

          - Finishes:  Manufacturer's standard painted finish and trim combination.

          - Wiring:  Sized for minimum of five No. 12 AWG power and ground conductors and a minimum of four, 4-pair, Category 3 or 5 voice and data communication cables.

          - Power Receptacles:  Two duplex, 20-A, heavy-duty, NEMA WD 6 configuration 5-20R units.

Coordinate subparagraph below with Division 27 Section "Communications Horizontal Cabling."

          - Voice and Data Communication Outlets:  Two RJ-45 Category 5e jacks.

      - FINISHES

See Editing Instruction No. 2 in the Evaluations for a discussion of wiring device colors.  Coordinate with Drawings.

        - Color:  Wiring device catalog numbers in Section Text do not designate device color.

          - Wiring Devices Connected to Normal Power System:  Ivory, unless otherwise indicated or required by NFPA 70 or device listing.

Delete first subparagraph below and edit paragraph and subparagraph above if a separate emergency power system serving wiring devices is not provided.

          - Wiring Devices Connected to Emergency Power System:  Red.

- EXECUTION

      - INSTALLATION

NECA 1 referenced in paragraph below includes device mounting-height requirements.  See "Product Selection and Application Considerations" Article in the Evaluations for device mounting heights in that standard.

        - Comply with NECA 1, including the mounting heights listed in that standard, unless otherwise noted.

See Editing Instruction No. 4 in the Evaluations for timing and sequencing of construction to assist in avoiding contamination of devices during construction.

        - Coordination with Other Trades:

          - Take steps to insure that devices and their boxes are protected.  Do not place wall finish materials over device boxes and do not cut holes for boxes with routers that are guided by riding against outside of the boxes.

          - Keep outlet boxes free of plaster, drywall joint compound, mortar, cement, concrete, dust, paint, and other material that may contaminate the raceway system, conductors, and cables.

          - Install device boxes in brick or block walls so that the cover plate does not cross a joint unless the joint is troweled flush with the face of the wall.

          - Install wiring devices after all wall preparation, including painting, is complete.

        - Conductors:

          - Do not strip insulation from conductors until just before they are spliced or terminated on devices.

          - Strip insulation evenly around the conductor using tools designed for the purpose.  Avoid scoring or nicking of solid wire or cutting strands from stranded wire.

          - The length of free conductors at outlets for devices shall meet provisions of NFPA 70, Article 300, without pigtails.

          - Existing Conductors:

            - Cut back and pigtail, or replace all damaged conductors.

            - Straighten conductors that remain and remove corrosion and foreign matter.

            - Pigtailing existing conductors is permitted provided the outlet box is large enough.

        - Device Installation:

          - Replace all devices that have been in temporary use during construction or that show signs that they were installed before building finishing operations were complete.

          - Keep each wiring device in its package or otherwise protected until it is time to connect conductors.

          - Do not remove surface protection, such as plastic film and smudge covers, until the last possible moment.

          - Connect devices to branch circuits using pigtails that are not less than 6 inches (152 mm) in length.

          - When there is a choice, use side wiring with binding-head screw terminals.  Wrap solid conductor tightly clockwise, 2/3 to 3/4 of the way around terminal screw.

          - Use a torque screwdriver when a torque is recommended or required by the manufacturer.

          - When conductors larger than No. 12 AWG are installed on 15- or 20-A circuits, splice No. 12 AWG pigtails for device connections.

          - Tighten unused terminal screws on the device.

          - When mounting into metal boxes, remove the fiber or plastic washers used to hold device mounting screws in yokes, allowing metal-to-metal contact.

        - Receptacle Orientation:

Retain subparagraph below if the position of the ground pin is important for consistency.  Trade and professional literature is inconsistent in recommending benefits of either orientation.

          - Install ground pin of vertically mounted receptacles up, and on horizontally mounted receptacles to the right.

Recommendation in subparagraph below is made in IEEE 602.

        - Device Plates:  Do not use oversized or extra-deep plates.  Repair wall finishes and remount outlet boxes when standard device plates do not fit flush or do not cover rough wall opening.

Coordinate two paragraphs below with Drawings.

        - Arrangement of Devices:  Unless otherwise indicated, mount flush, with long dimension vertical and with grounding terminal of receptacles on top.  Group adjacent switches under single, multigang wall plates.

        - Adjust locations of floor service outlets and service poles to suit arrangement of partitions and furnishings.

      - FIELD QUALITY CONTROL

        - Perform tests and inspections and prepare test reports.

          - Test Instruments:  Use instruments that comply with UL 1436.

          - Test Instrument for Convenience Receptacles:  Digital wiring analyzer with digital readout or illuminated LED indicators of measurement.

        - Tests for Convenience Receptacles:

          - Line Voltage:  Acceptable range is 105 to 132 V.

          - Percent Voltage Drop under 15-A Load:  A value of 6 percent or higher is not acceptable.

          - Ground Impedance:  Values of up to 2 ohms are acceptable.

          - GFCI Trip:  Test for tripping values specified in UL 1436 and UL 943.

          - Using the test plug, verify that the device and its outlet box are securely mounted.

          - The tests shall be diagnostic, indicating damaged conductors, high resistance at the circuit breaker, poor connections, inadequate fault current path, defective devices, or similar problems.  Correct circuit conditions, remove malfunctioning units and replace with new ones, and retest as specified above.

END OF SECTION 262726