Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 271500 - COMMUNICATIONS HORIZONTAL CABLING

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - UTP cabling.

          - 62.5/125-micrometer, optical fiber cabling.

          - Coaxial cable.

          - Multiuser telecommunications outlet assemblies.

          - Cable connecting hardware, patch panels, and cross-connects.

          - Telecommunications outlet/connectors.

          - Cabling system identification products.

          - Cable management system.

        - Related Requirements:

Retain subparagraphs below to cross-reference requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Section 280513 "Conductors and Cables for Electronic Safety and Security" for voice and data cabling associated with system panels and devices.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

        - BICSI:  Building Industry Consulting Service International.

        - Consolidation Point:  A location for interconnection between horizontal cables extending from building pathways and horizontal cables extending into furniture pathways.

        - Cross-Connect:  A facility enabling the termination of cable elements and their interconnection or cross-connection.

        - EMI:  Electromagnetic interference.

        - IDC:  Insulation displacement connector.

        - LAN:  Local area network.

        - Outlet/Connectors:  A connecting device in the work area on which horizontal cable or outlet cable terminates.

        - RCDD:  Registered Communications Distribution Designer.

        - UTP:  Unshielded twisted pair.

      - ADMINISTRATIVE REQUIREMENTS

Revise this article to specify coordination with other parties involved in finalizing communications equipment room work.  See Editing Instruction No. 3 in the Evaluations.

        - Coordinate layout and installation of telecommunications cabling with Owner's telecommunications and LAN equipment and service suppliers.

        - Coordinate telecommunications outlet/connector locations with location of power receptacles at each work area.

      - ACTION SUBMITTALS

        - Product Data:  For each type of product.

Retain subparagraph below for coaxial cable.  Installation data for UTP and optical fiber cabling are specified in the referenced TIA/EIA standards.

          - For coaxial cable, include the following installation data for each type used:

            - Nominal OD.

            - Minimum bending radius.

            - Maximum pulling tension.

Retain "Samples" Paragraph below when workstation outlet faceplates have critical features needing hands-on appraisal.

      - INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

        - Qualification Data:  For Installer, qualified layout technician, installation supervisor, and field inspector.

        - Source quality-control reports.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

      - CLOSEOUT SUBMITTALS

        - Maintenance Data:  For splices and connectors to include in maintenance manuals.

Retain "Software and Firmware Operational Documentation" Paragraph below for PC-based cabling administration systems.

      - MAINTENANCE MATERIAL SUBMITTALS

        - Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Device Plates:  One of each type.

      - QUALITY ASSURANCE

BICSI is an industry trade association.  See Editing Instruction No. 2 in the Evaluations for summaries of qualifications for registration.

        - Installer Qualifications:  Cabling Installer must have personnel certified by BICSI on staff.

          - Layout Responsibility:  Preparation of Shop Drawings, Cabling Administration Drawings, and field testing program development by an RCDD.

          - Installation Supervision:  Installation shall be under the direct supervision of Level 2 Installer, who shall be present at all times when Work of this Section is performed at Project site.

Delete "Testing Supervisor" Subparagraph below if Contractor performs field quality control.

          - Testing Supervisor:  Currently certified by BICSI as an RCDD to supervise on-site testing.

Retain "Testing Agency Qualifications" Paragraph below if Contractor or manufacturer selects testing agency or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article.  Qualification requirements are in addition to those specified in Section 014000 "Quality Requirements," which also defines "NRTL" (nationally recognized testing laboratory).

        - Testing Agency Qualifications:  An NRTL.

          - Testing Agency's Field Supervisor:  Currently certified by BICSI as an RCDD to supervise on-site testing.

      - DELIVERY, STORAGE, AND HANDLING

According to BICSI ITSIM, cables should be tested upon receipt.

        - Test cables upon receipt at Project site.

Retain one or both of first two subparagraphs below.

          - Test optical fiber cables to determine the continuity of the strand end to end.  Use optical fiber flashlight or optical loss test set.

          - Test optical fiber cables while on reels.  Use an optical time domain reflectometer to verify the cable length and locate cable defects, splices, and connector; including the loss value of each.  Retain test data and include the record in maintenance data.

          - Test each pair of UTP cable for open and short circuits.

- PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products.  For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

      - HORIZONTAL CABLING DESCRIPTION

        - Horizontal cable and its connecting hardware provide the means of transporting signals between the telecommunications outlet/connector and the horizontal cross-connect located in the communications equipment room.  This cabling and its connecting hardware are called a "permanent link," a term that is used in the testing protocols.

          - TIA/EIA-568-B.1 requires that a minimum of two telecommunications outlet/connectors be installed for each work area.

          - Horizontal cabling shall contain no more than one transition point or consolidation point between the horizontal cross-connect and the telecommunications outlet/connector.

          - Bridged taps and splices shall not be installed in the horizontal cabling.

          - Splitters shall not be installed as part of the optical fiber cabling.

        - The maximum allowable horizontal cable length is 295 feet (90 m).  This maximum allowable length does not include an allowance for the length of 16 feet (4.9 m) to the workstation equipment or in the horizontal cross-connect.

      - PERFORMANCE REQUIREMENTS

        - General Performance:  Horizontal cabling system shall comply with transmission standards in TIA/EIA-568-B.1 when tested according to test procedures of this standard.

        - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

        - Grounding:  Comply with J-STD-607-A.

      - UTP CABLE

Copy this article and re-edit for each product.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.  Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

          - ADC.

          - Belden Inc.

          - Berk-Tek; a Nexans company.

          - CommScope, Inc.

          - Draka Cableteq USA.

          - Genesis Cable Products; Honeywell International, Inc.

          - Mohawk; a division of Belden Networking, Inc.

          - Superior Essex Inc.

          - SYSTIMAX Solutions; a CommScope, Inc. brand.

          - 3M Communication Markets Division.

          - Tyco Electronics Corporation; AMP Products.

        - Description:  100-ohm, four-pair UTP, formed into 25-pair, binder groups covered with a blue thermoplastic jacket.

          - Comply with ICEA S-90-661 for mechanical properties.

          - Comply with TIA/EIA-568-B.1 for performance specifications.

          - Comply with TIA/EIA-568-B.2, Category 5e.

          - Listed and labeled by an NRTL acceptable to authorities having jurisdiction as complying with UL 444 and NFPA 70 for the following types:

Type requirements in subparagraphs below are minimum requirements and may be revised to suit Project.  Retain options if "permitted substitutions," as defined in NFPA 70, are appropriate for this Project.

            - Communications, Plenum Rated:  Type CMP, complying with NFPA 262.

            - Communications, Riser Rated:  Type CMR, complying with UL 1666.

      - UTP CABLE HARDWARE

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.  Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

          - American Technology Systems Industries, Inc.

          - Belden Inc.

          - Dynacom Inc.

          - Hubbell Premise Wiring.

          - Leviton Commercial Networks Division.

          - Molex Premise Networks; a division of Molex, Inc.

          - Panduit Corp.

          - Siemon Co. (The).

          - Tyco Electronics Corporation; AMP Products.

See Editing Instruction No. 4 in the Evaluations for discussion about 110-style IDC connectors and connector blocks.

        - General Requirements for Cable Connecting Hardware:  Comply with TIA/EIA-568-B.2, IDC type, with modules designed for punch-down caps or tools.  Cables shall be terminated with connecting hardware of same category or higher.

        - Connecting Blocks:  110-style IDC for Category 5e.  Provide blocks for the number of cables terminated on the block, plus 25 percent spare.  Integral with connector bodies, including plugs and jacks where indicated.

Delete "Cross-Connect" Paragraph below if cross-connection is accomplished exclusively on patch panels.

        - Cross-Connect:  Modular array of connecting blocks arranged to terminate building cables and permit interconnection between cables.

Coordinate "Number of Terminals per Field" Subparagraph below with Drawings for quantity of terminals.

          - Number of Terminals per Field:  One for each conductor in assigned cables.

        - Patch Panel:  Modular panels housing multiple-numbered jack units with IDC-type connectors at each jack for permanent termination of pair groups of installed cables.

Coordinate "Number of Jacks per Field" Subparagraph below with Drawings for quantity of fields.

          - Number of Jacks per Field:  One for each four-pair UTP cable indicated.

        - Jacks and Jack Assemblies:  Modular, color-coded, eight-position modular receptacle units with integral IDC-type terminals.

Cords are generally available in lengths to 20 feet (6 m) and longer in 24-inch (600-mm) increments.

        - Patch Cords:  Factory-made, four-pair cables in 36-inch (900 mm) lengths; terminated with eight-position modular plug at each end.

Retain one of two subparagraphs below; retain first for Category 6, second for Category 5e patch cords.

          - Patch cords shall have bend-relief-compliant boots and color-coded icons to ensure Category 6 performance.  Patch cords shall have latch guards to protect against snagging.

          - Patch cords shall have color-coded boots for circuit identification.

      - COAXIAL CABLE

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.  Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

          - Alpha Wire Company.

          - Belden Inc.

          - Coleman Cable, Inc.

          - CommScope, Inc.

          - Draka Cableteq USA.

See Evaluations for discussion about coaxial cables.  Indicate location of each type on Drawings.

        - Cable Characteristics:  Broadband type, recommended by cable manufacturer specifically for broadband data transmission applications.  Coaxial cable and accessories shall have 75-ohm nominal impedance with a return loss of 20 dB maximum from 7 to 806 MHz.

Cable types in first five paragraphs below are typical.

        - RG-11/U:  NFPA 70, Type CATV.

          - No. 14 AWG, solid, copper-covered steel conductor.

          - Gas-injected, foam-PE insulation.

          - Double shielded with 100 percent aluminum polyester tape and 60 percent aluminum braid.

          - Jacketed with sunlight-resistant, black PVC or PE.

          - Suitable for outdoor installations in ambient temperatures ranging from minus 40 to plus 85 deg C.

Paragraph below is typical of NFPA 70 cable types.  See NFPA 70, "Community Antenna Television and Radio Distribution Systems" and "Network-Powered Broadband Communications Systems" Articles for other types that may be added to the list.

        - NFPA and UL compliance, listed and labeled by an NRTL acceptable to authorities having jurisdiction as complying with UL 1655 and with NFPA 70 "Radio and Television Equipment" and "Community Antenna Television and Radio Distribution" Articles.  Types are as follows:

          - CATV Cable:  Type CATV.

          - CATV Plenum Rated:  Type CATVP, complying with NFPA 262.

          - CATV Riser Rated:  Type CATVR, complying with UL 1666.

          - CATV Limited Rating:  Type CATVX.

      - COAXIAL CABLE HARDWARE

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.  Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

          - Emerson Network Power Connectivity Solutions.

          - Leviton Commercial Networks Division.

          - Siemon Co. (The).

        - Coaxial-Cable Connectors:  Type BNC, 75 ohms.

      - CONSOLIDATION POINTS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.  Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

          - American Technology Systems Industries, Inc.

          - Belden Inc.

          - Chatsworth Products, Inc.

          - Dynacom Inc.

          - Hubbell Premise Wiring.

          - Molex Premise Networks; a division of Molex, Inc.

          - Ortronics, Inc.; a subsidiary of Legrand Group.

          - Panduit Corp.

          - Siemon Co. (The).

        - Description:  Consolidation points shall comply with requirements for cable connecting hardware.

Coordinate "Number of Terminals per Field" Subparagraph below with Drawings for quantity of terminals.

          - Number of Terminals per Field:  One for each conductor in assigned cables.

Coordinate "Number of Connectors per Field" Subparagraph below with Drawings for quantity of connectors.

          - Number of Connectors per Field:

            - One for each four-pair conductor group of indicated cables, plus 25 percent spare positions.

          - Mounting:  Recessed in ceiling.

          - NRTL listed as complying with UL 50 and UL 1863.

          - When installed in plenums used for environmental air, NRTL listed as complying with UL 2043.

      - TELECOMMUNICATIONS OUTLET/CONNECTORS

        - Jacks:  100-ohm, balanced, twisted-pair connector; four-pair, eight-position modular.  Comply with TIA/EIA-568-B.1.

Coordinate "Workstation Outlets" Paragraph below with other items specified to be mounted in workstation faceplates.  Revise paragraph if faceplate elevations are on Drawings.

        - Workstation Outlets:  Two-port-connector assemblies mounted in single faceplate.

Retain "Plastic Faceplate" or "Metal Faceplate" Subparagraph below, or retain both as required to match Section 262726 "Wiring Devices."

          - Plastic Faceplate:  High-impact plastic.  Coordinate color with Section 262726 "Wiring Devices."

          - For use with snap-in jacks accommodating any combination of UTP, optical fiber, and coaxial work area cords.

            - Flush mounting jacks, positioning the cord at a 45-degree angle.

Retain one of three "Legend" subparagraphs below; retain first for metal faceplates.

          - Legend:  Snap-in, clear-label covers and machine-printed paper inserts.

      - GROUNDING

        - Comply with requirements in Section 260526 "Grounding and Bonding for Electrical Systems" for grounding conductors and connectors.

        - Comply with J-STD-607-A.

      - IDENTIFICATION PRODUCTS

        - Comply with TIA/EIA-606-A and UL 969 for labeling materials, including label stocks, laminating adhesives, and inks used by label printers.

      - SOURCE QUALITY CONTROL

Retain "Testing Agency" Paragraph below if required.  Independent certification may be acceptable to authorities having jurisdiction without further monitoring of plant's quality-control and testing program by Owner.

        - Testing Agency:  Engage a qualified testing agency to evaluate cables.

        - Factory test UTP and optical fiber cables on reels according to TIA/EIA-568-B.1.

        - Factory test UTP cables according to TIA/EIA-568-B.2.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Factory-sweep test coaxial cables at frequencies from 5 MHz to 1 GHz.  Sweep test shall test the frequency response, or attenuation over frequency, of a cable by generating a voltage whose frequency is varied through the specified frequency range and graphing the results.

        - Cable will be considered defective if it does not pass tests and inspections.

        - Prepare test and inspection reports.

- EXECUTION

      - WIRING METHODS

Retain one of first two paragraphs below and coordinate with Drawings.  Delete both if wiring methods for system are indicated on Drawings.

        - Install cables in pathways and cable trays except within consoles, cabinets, desks, and counters and except in accessible ceiling spaces where unenclosed wiring method may be used.  Conceal pathways and cables except in unfinished spaces.

Retain first subparagraph below if retaining unenclosed wiring method option in paragraph above.

          - Install plenum cable in all locations.

          - Comply with raceway requirements in Section 260533.

        - Conceal conductors and cables in accessible ceilings, walls, and floors where possible.

        - Wiring within Enclosures:

          - Bundle, lace, and train conductors to terminal points with no excess and without exceeding manufacturer's limitations on bending radii.

          - Install lacing bars and distribution spools.

          - Install conductors parallel with or at right angles to sides and back of enclosure.

      - INSTALLATION OF CABLES

        - Comply with NECA 1.

        - General Requirements for Cabling:

          - Comply with TIA/EIA-568-B.1.

          - Comply with BICSI ITSIM, Ch. 6, "Cable Termination Practices."

          - Install 110-style IDC termination hardware unless otherwise indicated.

          - MUTOA shall not be used as a cross-connect point.

          - Consolidation points may be used only for making a direct connection to telecommunications outlet/connectors:

            - Do not use consolidation point as a cross-connect point, as a patch connection, or for direct connection to workstation equipment.

            - Locate consolidation points for UTP at least 49 feet (15 m) from communications equipment room.

          - Terminate conductors; no cable shall contain unterminated elements.  Make terminations only at indicated outlets, terminals, cross-connects, and patch panels.

          - Cables may not be spliced.  Secure and support cables at intervals not exceeding 30 inches (760 mm) and not more than 6 inches (150 mm) from cabinets, boxes, fittings, outlets, racks, frames, and terminals.

          - Install lacing bars to restrain cables, to prevent straining connections, and to prevent bending cables to smaller radii than minimums recommended by manufacturer.

          - Bundle, lace, and train conductors to terminal points without exceeding manufacturer's limitations on bending radii, but not less than radii specified in BICSI ITSIM, "Cabling Termination Practices" Chapter.  Install lacing bars and distribution spools.

          - Do not install bruised, kinked, scored, deformed, or abraded cable.  Do not splice cable between termination, tap, or junction points.  Remove and discard cable if damaged during installation and replace it with new cable.

          - In the communications equipment room, install a 10-foot- (3-m-) long service loop on each end of cable.

          - Pulling Cable:  Comply with BICSI ITSIM, Ch. 4, "Pulling Cable."  Monitor cable pull tensions.

        - UTP Cable Installation:

          - Comply with TIA/EIA-568-B.2.

          - Do not untwist UTP cables more than 1/2 inch (12 mm) from the point of termination to maintain cable geometry.

        - Open-Cable Installation:

          - Install cabling with horizontal and vertical cable guides in telecommunications spaces with terminating hardware and interconnection equipment.

          - Suspend UTP cable not in a wireway or pathway a minimum of 8 inches (200 mm) above ceilings by cable supports not more than 60 inches (1524 mm) apart.

          - Cable shall not be run through structural members or in contact with pipes, ducts, or other potentially damaging items.

        - Group connecting hardware for cables into separate logical fields.

See Editing Instruction No. 5 in the Evaluations for discussion about EMI.

        - Separation from EMI Sources:

          - Comply with BICSI TDMM and TIA-569-B for separating unshielded copper voice and data communication cable from potential EMI sources, including electrical power lines and equipment.

          - Separation between open communications cables or cables in nonmetallic raceways and unshielded power conductors and electrical equipment shall be as follows:

            - Electrical Equipment Rating Less Than 2 kVA:  A minimum of 5 inches (127 mm).

            - Electrical Equipment Rating between 2 and 5 kVA:  A minimum of 12 inches (300 mm).

            - Electrical Equipment Rating More Than 5 kVA:  A minimum of 24 inches (610 mm).

          - Separation between communications cables in grounded metallic raceways and unshielded power lines or electrical equipment shall be as follows:

            - Electrical Equipment Rating Less Than 2 kVA:  A minimum of 2-1/2 inches (64 mm).

            - Electrical Equipment Rating between 2 and 5 kVA:  A minimum of 6 inches (150 mm).

            - Electrical Equipment Rating More Than 5 kVA:  A minimum of 12 inches (300 mm).

          - Separation between communications cables in grounded metallic raceways and power lines and electrical equipment located in grounded metallic conduits or enclosures shall be as follows:

            - Electrical Equipment Rating Less Than 2 kVA:  No requirement.

            - Electrical Equipment Rating between 2 and 5 kVA:  A minimum of 3 inches (76 mm).

            - Electrical Equipment Rating More Than 5 kVA:  A minimum of 6 inches (150 mm).

          - Separation between Communications Cables and Electrical Motors and Transformers, 5 kVA or HP and Larger:  A minimum of 48 inches (1200 mm).

          - Separation between Communications Cables and Fluorescent Fixtures:  A minimum of 5 inches (127 mm).

      - FIRESTOPPING

        - Comply with TIA-569-B, Annex A, "Firestopping."

        - Comply with BICSI TDMM, "Firestopping Systems" Article.

      - GROUNDING

        - Install grounding according to BICSI TDMM, "Grounding, Bonding, and Electrical Protection" Chapter.

        - Comply with J-STD-607-A.

        - Bond metallic equipment to the grounding bus bar, using not smaller than No. 6 AWG equipment grounding conductor.

      - IDENTIFICATION

Retain one of first two paragraphs below.

        - Identify system components, wiring, and cabling complying with TIA/EIA-606-A.

See Evaluations for discussion about designating the class of cabling plant administration and color-coding of cross-connect fields.

See Evaluations for discussion about TIA/EIA standard as it applies to this Section.

        - Cable Schedule:  Post in prominent location in each equipment room and wiring closet.  List incoming and outgoing cables and their designations, origins, and destinations.  Protect with rigid frame and clear plastic cover.  Furnish an electronic copy of final comprehensive schedules for Project.

        - Cable and Wire Identification:

          - Label each cable within 4 inches (100 mm) of each termination and tap, where it is accessible in a cabinet or junction or outlet box, and elsewhere as indicated.

          - Each wire connected to building-mounted devices is not required to be numbered at device if color of wire is consistent with associated wire connected and numbered within panel or cabinet.

          - Exposed Cables and Cables in Cable Trays and Wire Troughs:  Label each cable at intervals not exceeding 15 feet (4.5 m).

          - Label each terminal strip and screw terminal in each cabinet, rack, or panel.

            - Individually number wiring conductors connected to terminal strips, and identify each cable or wiring group being extended from a panel or cabinet to a building-mounted device shall be identified with name and number of particular device as shown.

            - Label each unit and field within distribution racks and frames.

          - Identification within Connector Fields in Equipment Rooms and Wiring Closets:  Label each connector and each discrete unit of cable-terminating and connecting hardware.  Where similar jacks and plugs are used for both voice and data communication cabling, use a different color for jacks and plugs of each service.

        - Labels shall be preprinted or computer-printed type with printing area and font color that contrasts with cable jacket color but still complies with requirements in TIA/EIA-606-A.

          - Cables use flexible vinyl or polyester that flex as cables are bent.

      - FIELD QUALITY CONTROL

Retain "Testing Agency," "Manufacturer's Field Service," and "Perform the following tests and inspections" paragraphs below to identify who shall perform tests and inspections.  If retaining second option in "Testing Agency" Paragraph or if retaining "Manufacturer's Field Service" or "Perform the following tests and inspections" Paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

        - Testing Agency:  Engage a qualified testing agency to perform tests and inspections.

Retain "Manufacturer's Field Service" Paragraph below to require a factory-authorized service representative to perform tests and inspections.

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

        - Perform the following tests and inspections:

          - Visually inspect UTP and optical fiber cable jacket materials for NRTL certification markings.  Inspect cabling terminations in communications equipment rooms for compliance with color-coding for pin assignments, and inspect cabling connections for compliance with TIA/EIA-568-B.1.

          - Visually confirm Category 5e, marking of outlets, cover plates, outlet/connectors, and patch panels.

          - Visually inspect cable placement, cable termination, grounding and bonding, equipment and patch cords, and labeling of all components.

          - Test UTP backbone copper cabling for DC loop resistance, shorts, opens, intermittent faults, and polarity between conductors.  Test operation of shorting bars in connection blocks.  Test cables after termination but not cross-connection.

            - Test instruments shall meet or exceed applicable requirements in TIA/EIA-568-B.2.  Perform tests with a tester that complies with performance requirements in "Test Instruments (Normative)" Annex, complying with measurement accuracy specified in "Measurement Accuracy (Informative)" Annex.  Use only test cords and adapters that are qualified by test equipment manufacturer for channel or link test configuration.

          - UTP Performance Tests:

            - Test for each outlet.  Perform the following tests according to TIA/EIA-568-B.1 and TIA/EIA-568-B.2:

              - Wire map.

              - Length (physical vs. electrical, and length requirements).

              - Insertion loss.

              - Near-end crosstalk (NEXT) loss.

              - Power sum near-end crosstalk (PSNEXT) loss.

              - Equal-level far-end crosstalk (ELFEXT).

              - Power sum equal-level far-end crosstalk (PSELFEXT).

              - Return loss.

              - Propagation delay.

              - Delay skew.

Retain "Coaxial Cable Tests" Subparagraph below when cable is used for broadband closed-circuit television applications.  Revise to suit tests to verify cable performance for other systems using coaxial cable.

Retain "Final Verification Tests" Subparagraph below if Owner intends to use Contractor in final testing after its personnel have assumed the operation of communications system.

          - Final Verification Tests:  Perform verification tests for UTP systems after the complete communications cabling and workstation outlet/connectors are installed.

            - Voice Tests:  These tests assume that dial tone service has been installed.  Connect to the network interface device at the demarcation point.  Go off-hook and listen and receive a dial tone.  If a test number is available, make and receive a local, long distance, and digital subscription line telephone call.

            - Data Tests:  These tests assume the Information Technology Staff has a network installed and is available to assist with testing.  Connect to the network interface device at the demarcation point.  Log onto the network to ensure proper connection to the network.

        - Document data for each measurement.  Data for submittals shall be printed in a summary report that is formatted similar to Table 10.1 in BICSI TDMM, or transferred from the instrument to the computer, saved as text files, and printed and submitted.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - End-to-end cabling will be considered defective if it does not pass tests and inspections.

        - Prepare test and inspection reports.

END OF SECTION 271500