Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 280513 - CONDUCTORS AND CABLES FOR ELECTRONIC SAFETY AND SECURITY

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - UTP cabling.

          - Coaxial cabling.

          - RS-232 cabling.

          - RS-485 cabling.

          - Low-voltage control cabling.

          - Control-circuit conductors.

          - Fire alarm wire and cable.

          - Identification products.

      - DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

        - BICSI:  Building Industry Consulting Service International.

        - EMI:  Electromagnetic interference.

        - IDC:  Insulation displacement connector.

        - Low Voltage:  As defined in NFPA 70 for circuits and equipment operating at less than 50 V or for remote-control and signaling power-limited circuits.

        - Open Cabling:  Passing telecommunications cabling through open space (e.g., between the studs of a wall cavity).

        - RCDD:  Registered Communications Distribution Designer.

      - ACTION SUBMITTALS

        - Product Data:  For each type of product.

Retain subparagraph below for coaxial cable.  Installation data for UTP and optical fiber cabling are specified in the referenced TIA/EIA standards.

          - For coaxial cable, include the following installation data for each type used:

            - Nominal OD.

            - Minimum bending radius.

            - Maximum pulling tension.

      - INFORMATIONAL SUBMITTALS

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

        - Qualification Data:  For qualified layout technician, installation supervisor, and field inspector.

        - Source quality-control reports.

Retain "Field quality-control reports" Paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

      - QUALITY ASSURANCE

Retain "Testing Agency Qualifications" Paragraph below if Contractor or manufacturer selects testing agency or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article.  Qualification requirements are in addition to those specified in Section 014000 "Quality Requirements," which also defines "NRTL" (nationally recognized testing laboratory).  See Editing Instruction No. 2 in the Evaluations for discussion of qualifications of the RCDD designation.

        - Testing Agency Qualifications:  An NRTL.

          - Testing Agency's Field Supervisor:  Currently certified by BICSI as an RCDD to supervise on-site testing.

      - DELIVERY, STORAGE, AND HANDLING

According to BICSI ITSIM, telecommunications cables should be tested upon receipt.  Low-voltage wires and cables do not normally require testing before installation.

        - Test cables upon receipt at Project site.

Retain one or both of first two subparagraphs below.

          - Test each pair of UTP cable for open and short circuits.

      - FIELD CONDITIONS

        - Do not install conductors and cables that are wet, moisture damaged, or mold damaged.

          - Indications that wire and cables are wet or moisture damaged include, but are not limited to, discoloration and sagging of factory packing materials.

        - Environmental Limitations:  Do not deliver or install UTP, optical fiber, and coaxial cables and connecting materials until wet work in spaces is complete and dry, and temporary HVAC system is operating and maintaining ambient temperature and humidity conditions at occupancy levels during the remainder of the construction period.

- PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products.  For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

      - PERFORMANCE REQUIREMENTS

        - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

      - UTP CABLE

Copy this article and re-edit for each product.

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers:  Subject to compliance with requirements, provide products by the following:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.  Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

          - Belden Inc.

        - Description:  Belden cable 8444, 2 pair, twisted cable, 22 gauge.

Type requirements in subparagraphs below are minimum requirements and may be revised to suit Project.  Retain options if "permitted substitutions," as defined in NFPA 70, are appropriate for this Project.

      - UTP CABLE HARDWARE

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers:  Subject to compliance with requirements, provide products by the following:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.  Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

          - Belden Inc.

Type of connecting hardware depends on the equipment to which cable is connected.  Retain first paragraph below if UTP cable terminations are not specified with connected equipment.  Specifying connecting hardware here permits testing of cables before they are connected to the equipment.

        - UTP Cable Connecting Hardware:  IDC type, using modules designed for punch-down caps or tools.  Cables shall be terminated with connecting hardware of the same category or higher.

Revise paragraph below to match equipment requirements, or delete if connecting blocks are specified with the equipment.

        - Connecting Blocks:  110-style for Category 5e.  Provide blocks for the number of cables terminated on the block, plus 25 percent spare.  Integral with connector bodies, including plugs and jacks where indicated.

      - COAXIAL CABLE

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.  Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

          - Alpha Wire Company.

          - Belden Inc.

          - Coleman Cable, Inc.

          - CommScope, Inc.

          - Draka Cableteq USA.

See Evaluations for discussion of coaxial cables.  Indicate types on Drawings.

        - General Coaxial Cable Requirements:  Broadband type, recommended by cable manufacturer specifically for broadband data transmission applications.  Coaxial cable and accessories shall have 75-ohm nominal impedance with a return loss of 20 dB maximum from 7 to 806 MHz.

Cable types in first five paragraphs below are typical.

        - RG-11/U:  NFPA 70, Type CATV.

          - No. 14 AWG, solid, copper-covered steel conductor.

          - Gas-injected, foam-PE insulation.

          - Double shielded with 100 percent aluminum polyester tape and 60 percent aluminum braid.

          - Jacketed with sunlight-resistant, black PVC or PE.

          - Suitable for outdoor installations in ambient temperatures ranging from minus 40 to plus 85 deg C.

Paragraph below is typical of NFPA 70 cable types.  See NFPA 70 "Community Antenna Television and Radio Distribution Systems" and "Network-Powered Broadband Communications Systems" Articles for other types that may be used.

        - NFPA and UL Compliance:  Coaxial cables shall be listed and labeled by an NRTL acceptable to authorities having jurisdiction as complying with UL 1655, and with NFPA 70 "Radio and Television Equipment" and "Community Antenna Television and Radio Distribution" Articles.  Types are as follows:

Retain option in two of four subparagraphs below if "permitted substitutions," as defined in NFPA 70, are appropriate for this Project.

          - CATV Cable:  Type CATV.

          - CATV Plenum Rated:  Type CATVP, complying with NFPA 262.

      - COAXIAL CABLE HARDWARE

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.  Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

          - Emerson Network Power Connectivity Solutions; AIM Electronics Brand.

          - Leviton Commercial Networks Division.

          - Siemon.

        - Coaxial-Cable Connectors:  Type BNC, 75 ohms.

      - LOW-VOLTAGE CONTROL CABLE

        - Paired Cable: NFPA 70, Type CMG.

          - One pair, twisted, No. 18 AWG, stranded (19x30) tinned copper conductors.

          - PVC insulation.

          - Unshielded.

          - PVC jacket.

          - Flame Resistance: Comply with UL 1581.

        - Plenum-Rated, Paired Cable: NFPA 70, Type CMP.

          - One pair, twisted, No. 18 AWG, stranded (19x30) tinned copper conductors.

          - PVC insulation.

          - Unshielded.

          - PVC jacket.

          - Flame Resistance: Comply with NFPA 262.

      - CONTROL-CIRCUIT CONDUCTORS

        - Class 1 Control Circuits: Stranded copper, Type THHN-THWN, complying with UL 83, in raceway.

        - Class 2 Control Circuits: Stranded copper, Type THHN-THWN, complying with UL 83, in raceway.

        - Class 3 Remote-Control and Signal Circuits: Stranded copper, Type TW or TF, complying with UL 83.

      - IDENTIFICATION PRODUCTS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

        - Manufacturers:  Subject to compliance with requirements, provide products by one of the following:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed.  Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

          - Brady Worldwide, Inc.

          - HellermannTyton North America.

          - Kroy LLC.

          - Panduit Corp.

        - Comply with UL 969 for a system of labeling materials, including label stocks, laminating adhesives, and inks used by label printers.

      - SOURCE QUALITY CONTROL

Retain "Testing Agency" Paragraph below if required.  Independent certification may be acceptable to authorities having jurisdiction without further monitoring of plant's quality-control and testing program by Owner.

        - Testing Agency:  Engage a qualified testing agency to evaluate cables.

        - Factory test UTP and optical fiber cables on reels according to TIA/EIA-568-B.1.

        - Factory test UTP cables according to TIA/EIA-568-B.2.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - Factory sweep test coaxial cables at frequencies from 5 MHz to 1 GHz.  Sweep test shall test the frequency response, or attenuation over frequency, of a cable by generating a voltage whose frequency is varied through the specified frequency range and graphing the results.

        - Cable will be considered defective if it does not pass tests and inspections.

        - Prepare test and inspection reports.

- EXECUTION

      - WIRING METHOD

Coordinate this article with Drawings.  Retain one of three paragraphs below to specify wiring method.

        - Install wiring in metal pathways and wireways.

          - Minimum conduit size shall be 3/4 inch (21 mm).  Security control and data transmission wiring shall not share conduit with other building wiring systems.

          - Comply with requirements in Section 260533 "Raceway and Boxes for Electrical Systems."

        - Install cable, concealed in accessible ceilings, walls, and floors when possible.

        - Wiring within Enclosures:

          - Bundle, lace, and train conductors to terminal points with no excess and without exceeding manufacturer's limitations on bending radii.

          - Install lacing bars and distribution spools.

          - Separate power-limited and non-power-limited conductors as recommended in writing by manufacturer.

          - Install conductors parallel with or at right angles to sides and back of enclosure.

          - Connect conductors that are terminated, spliced, or interrupted in any enclosure associated with intrusion system to terminal blocks.

          - Mark each terminal according to system's wiring diagrams.

          - Make all connections with approved crimp-on terminal spade lugs, pressure-type terminal blocks, or plug connectors.

      - INSTALLATION OF CONDUCTORS AND CABLES

        - Comply with NECA 1.

        - Conductors:  Size according to system manufacturer's written instructions unless otherwise indicated.

        - General Requirements for Cabling:

          - Comply with TIA/EIA-568-B.1.

          - Comply with BICSI ITSIM, Ch. 6, "Cable Termination Practices."

          - Terminate all conductors; no cable shall contain unterminated elements.  Make terminations only at indicated outlets, terminals, and cross-connect and patch panels.

          - Cables may not be spliced.  Secure and support cables at intervals not exceeding 30 inches (760 mm) and not more than 6 inches (150 mm) from cabinets, boxes, fittings, outlets, racks, frames, and terminals.

          - Bundle, lace, and train conductors to terminal points without exceeding manufacturer's limitations on bending radii, but not less than radii specified in BICSI ITSIM, "Cabling Termination Practices" Chapter.  Install lacing bars and distribution spools.

          - Do not install bruised, kinked, scored, deformed, or abraded cable.  Do not splice cable between termination, tap, or junction points.  Remove and discard cable if damaged during installation and replace it with new cable.

          - Cold-Weather Installation:  Bring cable to room temperature before dereeling.  Heat lamps shall not be used for heating.

          - Pulling Cable:  Comply with BICSI ITSIM, Ch. 4, "Pulling Cable."  Monitor cable pull tensions.

Coordinate first paragraph below with UTP cable and hardware articles in Part 2.

        - UTP Cable Installation:  Install using techniques, practices, and methods that are consistent with Category 5e rating of components and that ensure Category 5e performance of completed and linked signal paths, end to end.

          - Comply with TIA/EIA-568-B.2.

          - Install 110-style IDC termination hardware unless otherwise indicated.

          - Do not untwist UTP cables more than 1/2 inch (12 mm) from the point of termination to maintain cable geometry.

See Editing Instruction No. 3 in the Evaluations for discussion of EMI.

        - Separation from EMI Sources:

          - Comply with BICSI TDMM and TIA-569-B recommendations for separating unshielded copper voice and data communication cable from potential EMI sources, including electrical power lines and equipment.

          - Separation between open communications cables or cables in nonmetallic raceways and unshielded power conductors and electrical equipment shall be as follows:

            - Electrical Equipment Rating Less Than 2 kVA:  A minimum of 5 inches (127 mm).

            - Electrical Equipment Rating between 2 and 5 kVA:  A minimum of 12 inches (300 mm).

            - Electrical Equipment Rating More Than 5 kVA:  A minimum of 24 inches (600 mm).

          - Separation between communications cables in grounded metallic raceways and unshielded power lines or electrical equipment shall be as follows:

            - Electrical Equipment Rating Less Than 2 kVA:  A minimum of 2-1/2 inches (64 mm).

            - Electrical Equipment Rating between 2 and 5 kVA:  A minimum of 6 inches (150 mm).

            - Electrical Equipment Rating More Than 5 kVA:  A minimum of 12 inches (300 mm).

          - Separation between cables in grounded metallic raceways and power lines and electrical equipment located in grounded metallic conduits or enclosures shall be as follows:

            - Electrical Equipment Rating Less Than 2 kVA:  No requirement.

            - Electrical Equipment Rating between 2 and 5 kVA:  A minimum of 3 inches (75 mm).

            - Electrical Equipment Rating More Than 5 kVA:  A minimum of 6 inches (150 mm).

          - Separation between Cables and Electrical Motors and Transformers, 5 kVA or HP and Larger:  A minimum of 48 inches (1200 mm).

          - Separation between Cables and Fluorescent Fixtures:  A minimum of 5 inches (127 mm).

      - POWER AND CONTROL-CIRCUIT CONDUCTORS

        - 120-V Power Wiring:  Install according to Section 260519 "Low-Voltage Electrical Power Conductors and Cables" unless otherwise indicated.

        - Minimum Conductor Sizes:

          - Class 1 remote-control and signal circuits, No. 14 AWG.

          - Class 2 low-energy, remote-control and signal circuits, No. 16 AWG.

          - Class 3 low-energy, remote-control, alarm and signal circuits, No. 12 AWG.

      - FIRESTOPPING

        - Comply with TIA-569-B, "Firestopping" Annex A.

        - Comply with BICSI TDMM, "Firestopping Systems" Article.

      - IDENTIFICATION

        - Identify system components, wiring, and cabling complying with TIA/EIA-606-A.

      - FIELD QUALITY CONTROL

Retain "Testing Agency," "Manufacturer's Field Service," and "Perform the following tests and inspections" paragraphs below to identify who shall perform tests and inspections.  If retaining second option in "Testing Agency" Paragraph or if retaining "Manufacturer's Field Service" or "Perform the following tests and inspections" Paragraph, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

Retain "Manufacturer's Field Service" Paragraph below to require a factory-authorized service representative to perform tests and inspections.

Retain "Perform the following tests and inspections" Paragraph below to require Contractor to perform tests and inspections.

        - Perform the following tests and inspections with the assistance of a factory-authorized service representative:

          - Visually inspect UTP and optical fiber cable jacket materials for NRTL certification markings.  Inspect cabling terminations to confirm color-coding for pin assignments, and inspect cabling connections to confirm compliance with TIA/EIA-568-B.1.

          - Visually inspect cable placement, cable termination, grounding and bonding, equipment and patch cords, and labeling of all components.

Retain first subparagraph below if verification of quality is to be performed before completion of the cabling.  Delete if cable connecting hardware is not retained in "UTP Cable" Article.

          - Test UTP cabling for DC loop resistance, shorts, opens, intermittent faults, and polarity between conductors.  Test operation of shorting bars in connection blocks.  Test cables after termination but not cross connection.

            - Test instruments shall meet or exceed applicable requirements in TIA/EIA-568-B.2.  Perform tests with a tester that complies with performance requirements in "Test Instruments (Normative)" Annex, complying with measurement accuracy specified in "Measurement Accuracy (Informative)" Annex.  Use only test cords and adapters that are qualified by test equipment manufacturer for channel or link test configuration.

Retain first subparagraph below if verification of quality is to be performed before completion of the cabling.  Delete if cable connecting hardware is not retained in "Optical Fiber Cable" Article.

Retain subparagraph below if verification of quality is to be performed before completion of the cabling.

        - Document data for each measurement.  Print data for submittals in a summary report that is formatted using Table 10.1 in BICSI TDMM as a guide, or transfer the data from the instrument to the computer, save as text files, print, and submit.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

        - End-to-end cabling will be considered defective if it does not pass tests and inspections.

        - Prepare test and inspection reports.

END OF SECTION 280513