Copyright 2008 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 281600 – SECURITY SYSTEMS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Intrusion detection with communication links to perform monitoring, alarm, and control functions.

Retain subparagraph below if integration of intrusion detection and other electronic systems is specified in this Section; delete if no integration is required.

Delete subparagraph below for standalone systems with no systems integration or for other projects with prime responsibility for systems integration specified in another Section.  For discussion of this concept, see "Systems Integration" Article in the Evaluations.

          - Integration of other electronic and electrical systems and equipment.

        - Related Sections:

Retain Sections in subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

          - Division 28 Section "Conductors and Cables for Electronic Safety and Security" for cabling between master control units and field-mounted devices and control units.

      - DEFINITIONS

Retain definition(s) remaining after this Section has been edited.

        - PhySec: Chief, Physical Security Division.

        - CCTV:  Closed-circuit television.

        - PIR:  Passive infrared.

        - RFI:  Radio-frequency interference.

        - UPS:  Uninterruptible power supply.

        - Control Unit:  System component that monitors inputs and controls outputs through various circuits.

        - Master Control Unit:  System component that accepts inputs from other control units and may also perform control-unit functions.  The unit has limited capacity for the number of protected zones and is installed at an unattended location or at a location where it is not the attendant's primary function to monitor the security system.

        - Monitoring Station:  Facility that receives signals and has personnel in attendance at all times to respond to signals.  A central station is a monitoring station that is listed.

        - Protected Zone:  A protected premises or an area within a protected premises that is provided with means to prevent an unwanted event.

In first paragraph below, adjust standard intruder's height, weight, and clothing to suit Project.

        - Standard Intruder:  A person who weighs 100 lb (45 kg) or less and whose height is 60 inches (1525 mm) or less; dressed in a long-sleeved shirt, slacks, and shoes.

In first paragraph below, adjust standard-intruder movement to suit Project.

        - Standard-Intruder Movement:  Any movement, such as walking, running, crawling, rolling, or jumping, of a "standard intruder" in a protected zone.

Retain first paragraph below if systems integration is specified in this Section.

        - Systems Integration:  The bringing together of components of several systems containing interacting components to achieve indicated functional operation of combined systems.

        - Zone.  A defined area within a protected premises.  It is a space or area for which an intrusion must be detected and uniquely identified.  The sensor or group of sensors must then be assigned to perform the detection, and any interface equipment between sensors and communication must link to master control unit.

      - SUBMITTALS

First five paragraphs below are defined in Division 01 Section "Submittal Procedures" as "action submittals."

        - Product Data:  Components for sensing, detecting, systems integration, and control, including dimensions and data on features, performance, electrical characteristics, ratings, and finishes.

Retain first paragraph below if custom equipment, such as operator panels and consoles, is specified in this Section.  Revise to suit Project and coordinate with Drawings.

        - Shop Drawings:  Detail assemblies of standard components that are custom assembled for specific application on this Project.

Retain first subparagraph below for integration with systems in other Sections.

          - Functional Block Diagram:  Show single-line interconnections between components including interconnections between components specified in this Section and those furnished under other Sections.  Indicate methods used to achieve systems integration.  Indicate control, signal, and data communication paths and identify programmable logic controllers, networks and control interface devices and media to be used.  Describe characteristics of network and other data communication lines.

Retain first four subparagraphs below if systems integration is specified in this Section.

            - Indicate methods used to achieve systems integration.

            - Indicate control, signal, and data communication paths and identify PLCs, networks, control interface devices, and media to be used.

            - Describe characteristics of network and other data communication lines.

            - Describe methods used to protect against power outages and transient voltages including types and ratings of isolation and surge suppression devices used in data, communication, signal, control, and ac and dc power circuits.

          - Raceway Riser Diagrams:  Detail raceway runs required for intrusion detection, access control, duress, CCTV, and for systems integration.  Include designation of devices connected by raceway, raceway type and size, and type and size of wire and cable fill for each raceway run.

          - UPS:  Sizing calculations.

Retain first subparagraph below for projects where conduit and cable routing is critical but only device locations are shown on Drawings.

          - Site and Floor Plans:  Indicate final outlet and device locations, routing of raceways, and cables inside and outside the building.  Include room layout for master control-unit console, terminal cabinet, racks, and UPS.

          - Master Control-Unit Console Layout:  Show required artwork and device identification.

Retain first subparagraph below for addressable systems.

          - Device Address List:  Coordinate with final system programming.

          - System Wiring Diagrams:  Include system diagrams unique to Project.  Show connections for all devices, components, and auxiliary equipment.  Include diagrams for equipment and for system with all terminals and interconnections identified.

          - Details of surge-protection devices and their installation.

          - Sensor detection patterns and adjustment ranges.

        - Equipment and System Operation Description:  Include method of operation and supervision of each component and each type of circuit.  Show sequence of operations for manually and automatically initiated system or equipment inputs.  Description must cover this specific Project; manufacturer's standard descriptions for generic systems are unacceptable.

Delete "Samples for Initial Selection" Paragraph above if colors and other characteristics are preselected and specified or scheduled.  Retain first paragraph below with or without above.

Remaining paragraphs are defined in Division 01 Section "Submittal Procedures" as "informational submittals."

Coordinate first paragraph below with qualification requirements in Division 01 Section "Quality Requirements" and as supplemented in "Quality Assurance" Article.

        - Qualification Data:  For Installer.

Retain first paragraph below if Contractor is responsible for field quality-control testing and inspecting.

        - Field quality-control reports.

        - Operation and Maintenance Data:  For intrusion detection system to include in emergency, operation, and maintenance manuals.  In addition to items specified in Division 01 Section "Operation and Maintenance Data," include the following:

          - Data for each type of product, including features and operating sequences, both automatic and manual.

          - Master control-unit hardware and software data.

        - Warranty:  Sample of special warranty.

        - Other Information Submittals:

          - Test Plan and Schedule:  Test plan defining all tests required to ensure that system meets technical, operational, and performance specifications within 60 days of date of Contract award.

          - Examination reports documenting inspections of substrates, areas, and conditions.

          - Anchor inspection reports documenting inspections of built-in and cast-in anchors.

      - QUALITY ASSURANCE

        - Installer Qualifications:

          - An employer of workers, at least one of whom is a technician certified by the National Burglar & Fire Alarm Association.

          - Manufacturer's authorized representative who is trained and approved for installation of units required for this Project.

Retain first paragraph below if systems integration is specified in this Section.

        - Intrusion Detection Systems Integrator Qualifications:  An experienced intrusion detection equipment supplier and Installer who has completed systems integration work for installations similar in material, design, and extent to that indicated for this Project, whose work has resulted in construction with a record of successful in-service performance.

Retain first paragraph below if Contractor selects testing agency or if Contractor is required to provide services of a qualified testing agency in "Field Quality Control" Article.  Qualification requirements are in addition to those specified in Division 01 Section "Quality Requirements," which also includes the definition for "NRTL" (nationally recognized testing laboratory).

        - Testing Agency Qualifications:  Member company of NETA or an NRTL.

          - Testing Agency's Field Supervisor:  Currently certified by NETA to supervise on-site testing.

        - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

        - Control Units, Devices, and Communications with Monitoring Station:  Listed and labeled by a qualified testing agency for compliance with SIA CP-01.

Retain first paragraph below if Owner requires FM Global approval.

        - FM Global Compliance:  FM-Approved and -labeled intrusion detection devices and equipment.

        - Comply with NFPA 70.

      - PROJECT CONDITIONS

        - Environmental Conditions:  Capable of withstanding the following environmental conditions without mechanical or electrical damage or degradation of operating capability:

Retain and revise conditions below and specify features required to provide satisfactory service.  See Editing Instruction No. 2 in the Evaluations.

          - Altitude:  Sea level to 4000 feet (1220 m).

          - Master Control Unit:  Rated for continuous operation in an ambient of 60 to 85 deg F (16 to 29 deg C) and a relative humidity of 20 to 80 percent, noncondensing.

          - Interior, Controlled Environment:  System components, except master control unit, installed in air-conditioned  interior environments shall be rated for continuous operation in ambients of 36 to 122 deg F (2 to 50 deg C) dry bulb and 20 to 90 percent relative humidity, noncondensing.

      - WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this article are not less than remedies available to Owner under prevailing local laws.

        - Special Warranty:  Manufacturer's standard form in which manufacturer and Installer agree to repair or replace components of intrusion detection devices and equipment that fail in materials or workmanship within specified warranty period.

Verify available warranties and warranty periods for units and components with manufacturers listed in Part 2 articles.  One-year warranty is industry standard for intrusion detection devices and equipment; some manufacturers provide two-year warranties if requested.

          - Warranty Period:  One year from date of Substantial Completion.

      - EXTRA MATERIALS

        - Furnish extra materials that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Intrusion Detection Devices:  Furnish quantity equal to five percent of the number of units of each type installed, but no fewer than one of each type.

          - Fuses:  Three of each kind and size.

          - Tool Kit:  Provide two sets of tools for use with security fasteners, each packaged in a compartmented kit configured for easy handling and storage.

          - Security Fasteners:  Furnish no fewer than 1 box for every 50 boxes or fraction thereof, of each type and size of security fastener installed.

- PRODUCTS

      - INTRUSION DETECTION SYSTEMS

        - The Contractor must design, procure, install, program, test, document and provide training for a complete TSA Office of Security approved Bosch intrusion detection system or approved equal turnkey system (i.e., Bosch 9412GV4 Intrusion Detection System and Hirsch System with Hirsch Velocity Access Control Software).

        - The Contractor will maintain and warranty the system for one (1) year after the acceptance date. The work will include, but may not be limited to the following:

          - Intrusion Detection Panel:

            - The type of panel to be installed will be a Bosch D9412GV4 intrusion detection system. The installer must be a certified Bosch vendor who is experienced in programming the advanced software features associated with this panel and which is required for this security application.

            - The host panel and all associated control equipment will be located in the Computer LAN/Server Room/Communications Room (refer to the floor plans for locations). A 360 degree (PIR) Sensor will be located inside of the LAN room. The IDS system will be standalone and not connected to the TSA network.

            - All equipment serving the IDS/Access Control system will be wall-mounted on the wall of the Computer LAN/Server Room/Communications Room.

            - Alarm Control Keypads Bosch D1265 Series touch-screen keypad or approved equivalent will be programmed to accept all password combinations and will have the capability to arm or disarm points designated as general office security points. PHYSEC will identify location in design intent or construction drawings.

            - The Contractor is responsible to ensure selected vendor is competent and current on the Bosch D9412GV4 Intrusion Detection System and Hirsch System with Hirsch Velocity Access Control Software.

            - The alarm system will notify, via a dedicated analog phone line provided by the local office, the respective/designated Federal Protective Service (FPS) Mega Center of the specified location, violations of the security system. It is the responsibility of the host office to ensure that there is a dedicated “Plain Old Telephone Line” (POTS) at each TSA location that has an approved security system installed.

            - The alarm system must be provided sufficient battery back-up to remain operational for a minimum of four (4) hours in the event of a power failure.

            - All intrusion detection devices will be centrally powered and monitored from the LAN Room.

            - A generic or universal PIN code will not be used to access TSA or FAM facilities.

            - The Contractor will be responsible for all the initial input of all user codes, HSPD-12 enrollment of all TSA personnel and completion of the FPS Mega Center Alarm Requirements Document (MARS) to be provided by the TSA Office of Security once the system has been installed and is ready for set-up and programming. Once the system is fully programmed, a copy of the Federal Protective Service (FPS) ALL EVENTS HISTORY REPORT will be provided to both FSD stall and TSA PSD at least 24 hours before arrival for system acceptance testing.

          - Intrusion Detection Sensors:

            - All devices will operate from 12VDC. Provide (necessary number to cover leased space) Bosch DS9360º panoramic Tri Tech ceiling-mounted 360 degree, motion detector or equal where specified and approved by TSA Office of Security.

            - Provide recessed magnetic ¾-inch door contact switches, Sentrol 1078C or equal where specified and approved by TSA Office of Security.

            - Provide overhead door contact switches, Sentrol 2200 or equal where specified and approved by TSA Office of Security.

            - Provide balanced magnetic switches for perimeter doors to collateral open storage spaces containing classified information, Harco HSD p/n 30000-00000-000.

          - Detector Cable Requirements:

            - All detectors will be connected via homeruns from the point of detection back to the IDS/Access Control Panel located in the LAN/Server Room.

            - Utilize Belden cable 8444, 2 pair, twisted cable, 22 gauge, CAT 5 or PHYSEC will specify equivalent.

            - All cable runs through conduit will require an additional pull string for future expansion and versatility.

          - Duress Alarm:

            - Utilize Belden cable 8444, 2 pair, twisted cable, 22 gauge, CAT 5, or TSA Office of Security-specified equivalent. The duress alarm button will be installed within reaching distance of the receptionist seating area so that it can be used covertly in an event of an emergency situation or event. The duress alarm button will be connected to and report as a Duress Alarm (on a dedicated zone or alarm point) through the IDS.

            - Signage will be erected inside TSA offices to advise of Duress/Strobes and procedures to follow: “DO NOT OPEN DOOR IF STROBE IS ACTIVE!”

      - ACCESS CONTROL

        - Electronic Access Control System:

          - The vendor selected by the Contractor to install this system must be a certified installer of the Access Control System.

          - Utilize Belden cable 8444, 2 pair, twisted cable, 22 gauge, CAT 5, or PHYSEC specified equivalent.

          - The selected vendor will have a full understanding of all current hardware and software applications.

          - Entry points of various levels of access and security requirements must be installed.

          - The Electronic Access Control System will work through the Intrusion Detection System Alarm Panel described above (Bosch/Radionics 9412GV4).

          - Hirsch Model DS47L-SSP-HID card readers will be installed to momentarily unlock the electronic strike while shunting the alarm and providing access control to the facility. Connect card readers to the Hirsch Digi-TRAC controller.

          - The following type of Hirsch mounting boxes will be used:

            - MB8 (ADA – preferred.

            - MB9 (ADA).

            - UMK Slope (ADA).

            - MB2SL (ADA).

            - MB20 (ADA).

          - All installation will utilize user-defined PINS.

          - Contractor will be responsible for all initial input of user-specified PINs and hand-carried media (fob/card) to meet the requirements of multifactor authentication.

          - Where airports utilize an access control card, all efforts should be made to allow users to utilize their issued access control media and PIN.

          - No perimeter or interior door will require or utilize any configuration of “Request-to-Exit” (REX) technology, other than for shunting the perimeter alarm system or where building construction requirements and/or local codes do not permit the use of capacitance push-bars or exit buttons.

          - The Hirsch Velocity Access Control System will have the capability to assign and at least 132,000 credentials per Hirsch.

        - Door Strikes:

          - Provide an electronic door strike.

          - All door strikes will be 24 Volts AC/DC or 12 Volts AC/DC.

          - All door strikes installed on all floors will be centrally powered from the LAN/Server Room.

          - All doors with use the Folgers Adam Model 310-3-1 electronic door strike or approved equal.

          - All doors without a deadbolt will utilize the Folders Adam Model 310-2 ¾ electric door strike or approved equal.

        - Electromagnetic Locks:

          - Provide an electromagnetic lock (MAG lock). Use Dyna Lock 3000 Series electromagnetic lock or approved equivalent.

          - All MAG locks will be 24 Volts AC.

          - All MAG locks installed on all floors are required to be centrally powered from the LAN/Server Room.

          - All MAG locks are required to provide sufficient battery back-up to remain operational for a minimum of four (4) hours in the event of a power failure.

          - All MAG locks will be installed in accordance with local building codes.

          - Intrusion Detection System (IDS) and Access Control System (ACS) must be integrated to ensure door props and forced entry alarms on access controlled doors.

          - The system will be programmed to report forced entry and/or a “prop open” alarm to the IDS system.

          - The installer will provide, as part of the installation, a Hirsch Client Management Station (Hirsch computer, monitor, reader, and server).

          - Contractor will provide training to multiple TSA personnel to enroll, update, and remove persons in the Hirsch system. NOTE: More than one person is to be trained to prevent single point of failure. At least three (3) hours of training will be conducted to ensure the local office is trained in the use and operation of all systems. Training one time upon installation will be conducted locally on-site and will ensure that there are an adequate number TSA personnel trained to Arm/Disarm and use the system correctly. Documentation that training was conducted to include class roster will be provided to the Federal Security Director (FSD)/Manager at location and also provided to TSA PSD.

      - VIDEO INTERCOM/DOOR ANSWERING SYSTEM, AIPHONE INCLUDING DOOR RELEASE

        - Contractor or Lessor will purchase, install, program, maintain, and test a turn-key Aiphone JK-1MED, or equivalent. (Note: Equivalent Video Intercom/Door Answering System must be approved by PHYSEC.) The Contractor or Lessor will provide authorized installers to install, program, maintain, and test the system. All equipment must be installed according to manufacturer’s specifications. All conduit sizing and wiring requirements are the responsibility of the Contractor or Lessor.

        - The Video Intercom/Door Answering System will have the capacity for additional door stations, either audio/video or audio only and up to two additional interior stations, either audio/video or audio only.

        - The external door station (outside door) must be a one-piece unit equipped with a CCD (Charged Coupled Device) chip camera with infrared LEDs (Liquid Electronic Displays) for low light applications. Pan/tilt mechanism adjustable by an interior monitor, call-in button, speaker/microphone for communication, and a locator LED. The call-in button on the external door station will turn on the 3/12-inch TFT color LCD at the inside monitor that initiates audio monitoring from the door and activates a two- or four-stroke chime. Audio communication at the external door station must be hands-free, and communication at the inside station must the through the handset.

        - The interior monitor station must be a one-piece unit equipped with a 3-1/2” flat TTF TFT color LCD monitor, a monitor activation button, a pan and tilt control pad, door release button, secondary dry contact (optional), an all call button, call-in indicator LED, and a handset for private communication. Brightness and chime volume controls must be located in each of the monitoring units. The entry area must have the ability to be monitored by pressing the “monitor”" button on any room station. This allows both audio and video monitoring, staying on for approximately 45 seconds. The interior stations must also be able to normally open a dry contact for door release and an extra dry contact for light or secondary door release activation.

        - Technical Specifications:

          - System: JK 1-MED Series; hands-free color video with pan tilt and zoom.

          - Power Source: 18V DC. Use PS-1820UL.

          - Communication:

            - Automatic (hands-free): To activate, momentarily push Talk button.

            - Talk Button, Manual (push-to-talk/relase-to-listen): To activate, push Talk button for 1 second or until talk LED turns on.

          - Calling: Chime, image, and audio approximately 45 seconds.

            - Between Inside Stations: All Call tone, then communicate with handset.

          - Video: Monitor; 3-1/2-inch direct-view TFT color LCD with 525 scanning lines.

          - Camera Unit: CCD (Charged Coupled Device) with infrared LED illumination.

          - Minimum Illumination: 5 lux at 1’-5/8” distance.

          - Night Viewing: Up to 1’-5/8” from camera with white LED projected, background beyond 1’-5/8” cannot be seen.

          - Wiring:

            - Door to Master: 2-cond., mid-cap, solid, non-shielded.

            - Master to Sub: 4-cond., mid-cap, solid, non-shielded.

            - Wiring Distance:

              - Door to Farthest Master/Sub-Master: 165 feet (22 AWG); 330 feet (18 AWG).

              - Master to IER-2: 245 feet (22 AWG); 490 feet (18 AWG).

            - Wire Type:

              - Master to Door: Aiphone #871802.

              - Between Masters/Sub: Aiphone #871804.

            - Mounting: Surface mount to a 1-gang box or ring.

            - Door Release Contact: Normally open, 12V AC, 0.4A max.

      - CCTV SYSTEMS

        - Closed Circuit TV (CCTV) Digital Video Recorder (DVR) Systems:

          - Where required, the Contractor is responsible for obtaining, installing, programming and testing a complete turn-key CCTV system approved by PHYSEC. The Contractor will maintain and warranty the system for one year after the acceptance date.

          - All installed CCTV cameras will be monitored at the reception desk and/or tenant specified location. The monitor(s) must be set up to display all cameras in a continuous loop and wired into the supplied Digital Video Recorder (DVR).

          - The CCTV cameras will be fixed mount and fixed zoom inside a smoke dome housing and must be installed so as to view and record all activity and persons entering/exiting TSA office space.

          - System hardware will include Contractor-provided:

            - Fixed mount all-weather IR/CCTV cameras Bosch Model WZ45 or approved equivalent.

            - Recording for a minimum of 25 days at 15 frames per second. Minimum 2 TB system.

            - Three 32-inch LCD wide screen color monitors. Locations specified on drawings.

            - All necessary hardware, wiring, power supplies.

            - Cameras.

          - Signage must be placed on interior of all perimeter doors indicating that property is protected by electronic video surveillance.

        - LAN Room:

          - The Alarm Control Panel (ACP), which is typically located in the LAN/Server Room should be located within 400 feet of any door employing any of the Intrusion Detection Systems or Electronic Access Control Systems components. A 360º Passive Infrared (PIR) motion sensor will be installed inside all LAN rooms. This space will be a separate zone on the Bosch panel or other approved system. LAN Room is specified as Information Security Restricted Areas (ISRA). All entry locations will use multifactor authentication access control (e.g., card key and PIN) to access the area.

          - Signage: Sensitive areas (e.g., rooms containing information system servers, controlled interface equipment, associated peripherals, communication equipment, etc.) or areas where restricted actions occur (e.g., information assurance monitoring, system administration, etc.) will be deemed an Information Security Restricted Area (ISRA) and clearly labeled as an “Information Security Restricted Area.”

        - Kaba E-PLEX 5800 Series (as designated by FSD Staff):

          - The E-PLEX 5800 Door Control System will work as a standalone system.

          - The key-operated lock housing must accept a Medeco UL 437 M-3 interchangeable core.

          - M3 cores must be “large format” to fit in the Kaba E-PLEX. The client’s identity (TSA) and where the locks are installed will be not be divulged except as agreed upon by TSA.

          - The E-PLEX Door Control System will have the capability to assign and monitor no fewer than 3000 unique Personal Identification Numbers (PIN).

          - The E-PLEX Door Control System will have the capability to assign and monitor no fewer than 3000 HSPD-12 (PIV) cards. System will include KAVA E-PLEX FIPS general implementation kit and enrollment station laptop PC, commercial, off-the-shelf, not TSA networked, and E-PLEX 5800 FIPS/DES Fire Card Reader/Enroller and E-PLEX 5800 General FIPS software.

          - LPM-1000 Lock Programming Module with FIPS 201 Enroller.

          - The Contractor will be responsible for all programming including the initial input of user data and codes and completion of the tracking spreadsheet document. All TSA employees will be programmed into E-PLEX 5800 with HSPD12 card and unique PIN # for each employee.

          - Contractor will provide training to TSA personnel to enroll and remove persons at the lock. NOTE: More than person is to be trained to prevent single point of failure. At least three hours of training will be provided on operation of KABA 5800 at airport locations and/or adjacent offices as needed.

          - Contractor will provide documentation from KABA showing proof of certification to install and program the E-PLEX.

        - Security System Installer Information Requirements:

          - Upon request by the TSA Office of Security, the local TSA staff, or OSO, Compliance  Surface Inspections, the Contractor will be required to provide the following information about the Contractor’s employees and subcontractors who may have direct or incidental access to information being provided by the TSA:

            - Employee’s full name.

            - Employee’s date and place of birth.

            - Employee’s social security number.

            - Employee’s race and sex.

            - Complete fingerprint card.

            - General Release of Information document.

          - The Contractor is required to use GSA schedules and/or other government discounts when purchasing equipment or services on behalf of the TSA.

          - All program software and written materials pertaining to the security/access control system and related devices will be turned over to the TSA Office of Security, to include:

            - Detailed line item cost proposals.

            - Product specification sheets.

            - Inventory lists.

            - Operating and installation instructions.

            - As-built drawings.

            - Key cut and pinning charts for locking system.

          - All questions pertaining to the security devices and their operation must be directed to the TSA Office of Physical Security. Under no circumstances will Statements of Work (SOW) written by the TSA Office of Security, Physical Security Division be changed or modified without the express written permission of this office.

        - Contractor is responsible for the following:

          - All conduit sizing and installation are the responsibility of the Contractor, if required by the facility.

          - Complete system with Hirsch Model DS47L-SSP-HID card readers, computer, and enrollment station.

          - Bosch D9412GV4 Intrusion Detection System and duress buttons with strobes to include strobes mounted outside TSA spaces to alert LAS airport of duress activation.

          - Bosch D1265 Touch Screen Keypad/Disarm Keypads connected to Bosch D9412GV4 Intrusion Detection System.

          - Bosch DS9360 Ceiling-Mount Panoramic TriTech Motion Detectors connected to Bosch D9412GV4 Intrusion Detection System.

          - Door Contact Switches Bosch D9412GV4 Intrusion Detection System.

          - Folgers Adam Model 310-3-1 and 310-1-2/3 electronic door strikes or HES equivalent on doors.

          - Complete, turn-key CCTV/DVR system (to include cameras).

          - Heavy-duty door closers for all doors.

          - All wiring and hardware.

          - Installation of all security systems and/or devices will be in accordance with manufacturer’s requirements.

          - The personnel installing and programming security systems will be certified and current with the manufacturer.

          - All locksmith personnel installing, keying, pinning locks and other security devices will be certified, and current with the manufacturer.

          - Copies of all certifications and/or completed training will be available for review on-site.

          - Contractor will submit to TSA CSO a detailed line item cost breakdown for all security material and employee hours billed to the United States Government. Contractor will provide a detailed installation schedule to TSA CSO as part of the proposal submitted by the Contractor. Contractor will also immediately advise TSA CSO in writing of any delays.

          - The United States Government has the right to inspect and test all supplies called for in the contract, to the extent practicable, at all places and times and in in any event before acceptance in any manner that does not unduly delay the work.

          - The only person authorized to accept completion of security system installation projects on behalf of the United States Government/Transportation Security Administration (TSA) is an Inspector SV 1801 who is also current and certified as a Contract Officer’s Representative (COR) with certifications on file with TSA Office of Acquisitions.

          - During the acceptance phase, the Contractor will provide a binder with copies of manufacturer brochures and any floor plans or drawings for all security systems and/or devices installed.

          - Substitution of security systems and/or devices with “equivalent”, “same as”, or other terms in this manner is not authorized unless approved by the COTR, prior to installation.

          - The COR is not authorized to delete, change, waive, or negotiate any of the technical requirements or other terms and conditions of the contract. Should a change (monetary or otherwise) to the contract become necessary, it must be made by a contract modification issued by the Contracting Officer.

Retain subparagraph below if retaining "supervisory," option in paragraph above.

Retain one of first two paragraphs below.  See "Control Units" Article in the Evaluations.

Coordinate function in first paragraph below with timing device specified in "Master Control Unit" Article.

Retain first paragraph below if alarm signals control lights, elevators, intercom, sound, or CCTV components.  Revise to suit Project design and systems integration specifications.  Coordinate with Drawings.

Retain first paragraph below for system with printer.

Two-second maximum time in first paragraph below applies to hard-wired systems.  Multiplexed systems may require longer times.

"Programmed Secure-Access Control" Paragraph below is an optional feature.  Coordinate with Drawings.

- EXECUTION

      - EXAMINATION

        - Examine substrates, areas, and conditions, with Installer present, for compliance with requirements for installation tolerances and other conditions affecting performance of intrusion detection.

        - Examine roughing-in for embedded and built-in anchors to verify actual locations of intrusion detection connections before intrusion detection installation.

        - Prepare written report, endorsed by Installer, listing conditions detrimental to performance of intrusion detection.

        - Inspect built-in and cast-in anchor installations, before installing intrusion detection, to verify that anchor installations comply with requirements.  Prepare inspection reports.

          - Remove and replace anchors where inspections indicate that they do not comply with requirements.  Reinspect after repairs or replacements are made.

          - Perform additional inspections to determine compliance of replaced or additional anchor installations.  Prepare inspection reports.

        - For material whose orientation is critical for its performance as a ballistic barrier, verify installation orientation.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - SYSTEM INTEGRATION

Retain this article to integrate intrusion detection system with other systems.  See Evaluations for discussion of systems integration.  Also see definition of term "systems integration" in "Definitions" Article.

        - Integrate the following systems and equipment:

Revise list below to include only items in Project that require integration with intrusion detection system.

          - Electronic door hardware.

          - Intercommunications and program systems.

          - Access control.

          - Fire-alarm system.

          - Perimeter security system.

          - Video surveillance.

      - SYSTEM INSTALLATION

        - Comply with UL 681 and NFPA 731.

Retain first paragraph below for equipment supported on finished floor.

        - Equipment Mounting:  Install master control unit on finished floor with tops of cabinets not more than 72 inches (1830 mm) above the finished floor.

Retain subparagraph below if Project requires seismic bracing.  Coordinate with Division 26 Section "Vibration and Seismic Controls for Electrical Systems."

        - Install wall-mounted equipment, with tops of cabinets not more than 72 inches (1830 mm) above the finished floor.

Retain subparagraph below if Project requires seismic bracing.  Coordinate with Division 26 Section "Vibration and Seismic Controls for Electrical Systems."

          - Comply with requirements for seismic-restraint devices specified in Division 26 Section "Vibration and Seismic Controls for Electrical Systems."

      - WIRING INSTALLATION

Coordinate this article with Drawings.

Retain one of first two "Wiring Method" paragraphs below if wiring method for intrusion detection system is not specified in Division 26 Section "Raceway and Boxes for Electrical Systems." Delete first two paragraphs and retain and revise third paragraph to suit Project.

        - Wiring Method:  Install wiring in metal raceways according to Division 26 Section "Raceway and Boxes for Electrical Systems." Conceal raceway except in unfinished spaces and as indicated.  Minimum conduit size shall be 1/2 inch (13 mm).  Control and data transmission wiring shall not share conduit with other building wiring systems.

        - Wiring Method:  Cable, concealed in accessible ceilings, walls, and floors when possible.

        - Wiring within Enclosures:  Bundle, lace, and train conductors to terminal points.  Use lacing bars and distribution spools.  Separate power-limited and non-power-limited conductors as recommended in writing by manufacturer.  Install conductors parallel with or at right angles to sides and back of enclosure.  Connect conductors that are terminated, spliced, or interrupted in any enclosure associated with intrusion system to terminal blocks.  Mark each terminal according to system's wiring diagrams.  Make all connections with approved crimp-on terminal spade lugs, pressure-type terminal blocks, or plug connectors.

        - Wires and Cables:

Coordinate subparagraphs below with Drawings.

          - Conductors:  Size as recommended in writing by system manufacturer unless otherwise indicated.

          - 120-V Power Wiring:  Install according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables" unless otherwise indicated.

          - Control and Signal Transmission Conductors:  Install unshielded, twisted-pair cable unless otherwise indicated or if manufacturer recommends shielded cable, according to Division 28 Section "Conductors and Cables for Electronic Safety and Security."

          - Data and Television Signal Transmission Cables:  Install according to Division 28 Section "Conductors and Cables for Electronic Safety and Security."

        - Splices, Taps, and Terminations:  Make connections only on numbered terminal strips in junction, pull, and outlet boxes; terminal cabinets; and equipment enclosures.

        - Install power supplies and other auxiliary components for detection devices at control units unless otherwise indicated or required by manufacturer.  Do not install such items near devices they serve.

        - Identify components with engraved, laminated-plastic or metal nameplate for master control unit and each terminal cabinet, mounted with corrosion-resistant screws.  Nameplates and label products are specified in Division 26 Section "Identification for Electrical Systems."

      - IDENTIFICATION

        - Identify system components, wiring, cabling, and terminals.  Comply with identification requirements in Division 26 Section "Identification for Electrical Systems."

        - Install instructions frame in a location visible from master control unit.

      - GROUNDING

        - Ground the master control unit and associated circuits; comply with IEEE 1100.  Install a ground wire from main service ground to master control unit.

        - Ground system components and conductor and cable shields to eliminate shock hazard and to minimize ground loops, common-mode returns, noise pickup, cross talk, and other impairments.

Coordinate paragraph below with Drawings.

      - FIELD QUALITY CONTROL

        - Pretesting:  After installation, align, adjust, and balance system and perform complete pretesting to determine compliance of system with requirements in the Contract Documents.  Correct deficiencies observed in pretesting.  Replace malfunctioning or damaged items with new ones and retest until satisfactory performance and conditions are achieved.  Prepare forms for systematic recording of acceptance test results.

          - Report of Pretesting:  After pretesting is complete, provide a letter certifying that installation is complete and fully operable; include names and titles of witnesses to preliminary tests.

Retain one of first three paragraphs below to identify who shall perform tests and inspections.  If retaining second option in first paragraph, or if retaining second or third paragraph, retain "Field quality-control reports" Paragraph in "Submittals" Article.

        - Testing Agency:  Engage a qualified testing agency to perform tests and inspections.

Retain first paragraph below to require a factory-authorized service representative to perform inspections, tests, and adjustments.

Retain first paragraph below to require Contractor to perform tests and inspections.

        - Perform tests and inspections.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.

          - Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Retain first paragraph below to describe tests and inspections to be performed.

        - Tests and Inspections:  Comply with provisions in NFPA 731, Ch. 9, "Testing and Inspections."

          - Inspection:  Verify that units and controls are properly labeled and interconnecting wires and terminals are identified.

          - Test Methods:  Intrusion detection systems and other systems and equipment that are associated with detection and accessory equipment shall be tested according to Table "Test Methods" and Table "Test Methods of Initiating Devices."

        - Documentation:  Comply with provisions in NFPA 731, Ch. 4, "Documentation."

        - Tag all equipment, stations, and other components for which tests have been satisfactorily completed.

      - ADJUSTING

Revise this article to suit Project.

        - Occupancy Adjustments:  When requested within 12 months of date of Substantial Completion, provide on-site assistance in adjusting system to suit actual occupied conditions.  Provide up to three visits to Project during other-than-normal occupancy hours for this purpose.  Visits for this purpose shall be in addition to any required by warranty.

      - DEMONSTRATION

        - Train Owner's maintenance personnel to adjust, operate, and maintain the systems as outlined in each section.

END OF SECTION 281600