Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 283111M - FIRE ALARM SYSTEM MODIFICATIONS

- GENERAL

      - DESCRIPTION OF WORK

        - Scope:  Provide a fire alarm system modification, with associated equipment, ready for operation.

        - Description of Work:  The majority of work includes designing and installing new fire alarm devices as described herein and on the contract drawings for the TSA Tenant renovation and fit-out on the Second Floor of the Portland Jetport building in Portland, Maine.  The new design and installation includes all wiring, raceways, pull boxes, terminal cabinets, outlet and mounting boxes, control equipment, alarm and supervisory signal initiating devices, alarm indicating devices, and all other accessories and miscellaneous items required for a complete operating system.  In addition, the following items must be incorporated into the project:

          - Provide new fire alarm speakers (wall mounted for the project area shown on the drawings) to provide adequate coverage and distribution to ensure the audibility sound level requirements in NFPA 72 are met.  The new fire alarm speakers shall be compatible with the building's existing fire alarm system.  Depending on the layout, additional power supplies may be required. To ensure audible signals are clearly heard, the sound level shall be at least 70dBA throughout the project area (see drawings). The quantities and locations of fire alarm speakers shown on the drawings are for cost estimating purposes only.  Additional speakers shall be provided, if necessary, to meet minimum sound level requirements specified above.

          - Provide new fire alarm strobes for the project area to provide adequate coverage and distribution to ensure the visibility level requirements in NFPA 72 are met.  The new fire alarm strobes shall be compatible with the building's existing fire alarm system.  Provide all required auxiliary power supply panels, conduit, wiring, control devices, software, programming, etc. to provide a fully functional system in accordance with NFPA 72 requirements.  Combination speaker/strobes are acceptable.

        - Existing Fire Alarm Equipment:  Maintain existing fire alarm equipment outside of any area(s) under construction fully operational.  Furthermore, as necessary for tie-ins, the existing fire alarm system and equipment can be taken out of service only during construction periods in which the system is being modified and the Contractor is at the work-site.  Prior to leaving the work-site each day the Contractor shall restore the fire alarm system to service.  All new devices installed shall be compatible with the existing fire alarm system.

Maintain existing fire alarm equipment fully operational.  As new equipment is installed, label it "NOT IN SERVICE" until it is accepted.

        - Equipment Removal:  Remove all existing equipment not to be reused, including wiring, raceways, conduit, boxes, cabinets, outlets, mounting boxes and other devices, and restore all damaged surfaces as specified herein. Remove the remainder of the existing materials from the site and dispose of them.

        - Compliance:  Design and install the entire fire alarm system in accordance with Section 1.2E of this specification, except where modified herein.  All equipment and materials used shall be listed or approved by UL, FM, or another nationally recognized testing agency approved by the Contracting Officer, for their intended use and service.

        - Related Sections and Divisions:

          - Refer to these Division 16 specifications for related guidance:

            - Cable

            - Wire

            - Raceways

            - Connectors

          - Refer to this Division-7 specification for related guidance:

            - Firestopping

      - QUALITY ASSURANCE

        - Specialist Requirements:  Design shall be by a Registered Fire Protection Engineer or by a NICET Level III or IV Technician and certified by a Registered Fire Protection Engineer.  Installation must be performed by an electrical contractor with at least three (3) years experience in the design and installation of fire alarm systems.  Design and installation must be performed by an electrical contractor whose business is located within 75 miles of Portland, ME and whose business has been operated and established within this radius for at least three (3) years.

Prior to installation, the contractor must submit the following:

          - Data showing that the contractor has successfully installed fire alarm systems of the same type and design as specified herein; or, that the contractor has a firm contractual agreement with a subcontractor having such experience;

          - The names and locations of at least two installations where the contractor or subcontractor installed such systems; and

          - Data certifying that each system has performed satisfactorily for a period of not less than one year.

        - Project Superintendent: The contractor, or subcontractor, shall provide one full-time, on-site staff member designated as the "Project Superintendent".  The duties of the Project Superintendent are to supervise execution of all aspects of this specification, including safety on the job site as described in the "Accident Prevention Clause" of the general provisions of the Occupational Safety and Health (OSH) Act of 1970.  That clause incorporates into the contract, by reference, the Secretary of Labor's OSH Standards (29 CFR Part 1926).  The Project Superintendent shall be thoroughly familiar with all contract obligations and shall be capable of making all contractual decisions with regards to their project scope of work on behalf of the contractor, or subcontractor.  The Project Superintendent shall be responsible for making sure that quality control review has been performed on all submittals prior to the submission to the contracting officer.  The Project Superintendent shall also be responsible for ensuring that all submittals are accurate and fully coordinated.

        - Service Organization:  The contractor shall furnish evidence that there is an experienced and effective service organization that carries a stock of repair parts for the system to be furnished.  Should the contractor fail to comply with the service requirements of this section, the government will then have the option to make the necessary repairs and back charge the contractor without any loss of warranty or guarantee as provided by the contract documents.

        - Guarantee:  All equipment and materials provided under this contract must be new. The contractor shall guarantee labor, materials, and equipment provided under this contract against defects for a period of one year after the date of final acceptance of this work by the government and the receipt of as-built drawings and schematics of all equipment.  Replacement parts for the system furnished under this contract shall be available for at least ten years after the date of final acceptance of this work by the Government.

        - Codes and Standards:  Provide a fire alarm system conforming to the latest editions of codes and standards of the following organizations:

          - National Fire Protection Association (NFPA), including all amendments and appendices:

NFPA No. 70: National Electrical Code (NEC)

NFPA No. 72: National Fire Alarm Code

          - Factory Mutual Engineering and Research Corporation (FM):

FM-P7825 Approval Guide

          - Underwriter's Laboratories Inc. (U.L.):

UL-FPED Fire Protection Equipment Directory

UL Electrical Construction Materials Directory

UL 217 Single and Multiple Station Smoke Detectors

UL 268 Smoke Detectors for Fire Protective Signaling Systems

UL 864 Control Units for Fire Protection Signaling Systems

UL 1971 Signaling Devices for the Hearing Impaired

          - Other GSA-approved testing laboratories

          - International Code Council (ICC) International Code Council (ICC), including all supplements:

International Building Code

International Fire Code

          - GSA Facilities Standards for the Public Buildings Service – PBS-P100

          - Maine Uniform Building and Energy Code

          - Portland Fire Department Requirements

      - DEFINITIONS

        - General:  Wherever mentioned in this specification or on the drawings, define the equipment, devices, and functions as follows:

          - Alarm Signal:  A signal indicating an emergency requiring immediate notification of the fire department and of the building occupants.  These are signals such as:

            - The activation of a manual pull station.

            - The activation of a waterflow switch from a sprinkler system.

            - The activation of a ceiling-mounted spot-type smoke detector after it has undergone alarm confirmation.

          - Supervisory Signal:  A signal indicating the impairment of a fire protection system that may prevent its normal operation.  These are signals such as the operation of a valve tamper switch, low air pressure switch, duct smoke detector, etc.

          - Trouble Signal:  A signal which indicates that a fault, such as an open circuit or ground, has occurred in the system, or that the system has lost power.

          - Class A Wiring:  Class A circuits are electrically supervised such that a single break or single ground fault condition will be indicated by a trouble signal on the fire alarm control panel (FACP).  The circuit shall be capable of operation for its intended service with a single break or ground fault no matter where the break or ground fault condition occurs.

          - Class B Wiring:  Class B circuits are electrically supervised such that a single break or a single ground fault condition will be indicated by a trouble signal on the FACP no matter where the break or ground fault condition occurs.

          - Verified Smoke Detection:  The use of a smoke detection system with an alarm verification process.  The verification process interrupts the transmission of an alarm signal from a smoke detector for a designated time period (less than one minute).  Immediately following the interruption period, if the smoke detector is still in alarm, an alarm signal will be sent to the control panel to initiate the next event in the sequence of operation.

      - SYSTEM OPERATION

        - General:  The building's existing fire alarm system operation shall remain unchanged except for the relocation of existing and/or the installation of the new fire alarm devices as indicated on the drawings and specified herein.

          - A minimum of two (2) distinct fire alarm audible notification appliance circuits and a minimum of two (2) distinct visible notification appliance circuits shall be provided.  The system must be designed and installed so that a single wire to wire short or any other single Class B impairment on an audible or visible NAC does not affect more than one half of the area.

      - ELECTRICAL SUPERVISION

        - System Supervision:  Provide a system having electrical supervision in accordance with NFPA 72.  Indicate an open on a circuit by zone with a trouble signal at the FACP.  Indicate a ground fault by a trouble signal at the FACP.

          - Provide Class B notification appliance circuit such that a single fire will not affect more one half of the area.

      - SUBMITTALS

        - Division 1:  Conform to the requirements of Division-1 Section "Submittals."  Submit 6 complete sets of submittals.  Partial submittals will not be accepted and will be returned without review.  All submittals must be signed/stamped by the individual who designed the system.  Before any work is started, the engineer of record must approve the submittal.

In the submittal, provide manufacturer's data for the following and annotate the data to show the specific model, voltage, catalog numbers, type, etc.

          - Fire Alarm Audio Devices (Speakers)

          - Fire Alarm Strobes

          - All Wiring

          - All Conduit

          - Auxiliary Power and/or Control Panels

          - Terminal Cabinets

        - Shop Drawings:  Submit detailed shop drawings, on uniform size sheets no smaller than 30 by 42 inches, to the Contracting Officer for review and approval.  Before any work is started, the engineer of record must approve the shop drawings. Provide the following on the shop drawings:

          - Complete schematic circuit diagrams for all equipment including panel modules.

          - Point-to-point wiring diagrams showing the points of connection and terminals used for all electrical field connections in the system. Include all interconnections between the fire alarm control panel and all new equipment, devices, or systems that are supervised or controlled by the system.  Diagrams shall show all connections from the new field devices to the control panel, initiating and indicating circuits, switches, relays and terminals.

          - A complete description of the system operation.  In detailed narrative form, explain how the system will operate/function upon activation of the various alarm initiating devices such as pull stations, sprinkler system waterflow switches, sprinkler system control valve tamper switches, elevator lobby smoke detectors, air-handling unit smoke detectors, etc.  All events that will automatically occur upon activation of any of these different devices shall be fully explained and detailed in writing.

          - A schedule of zones.

          - Complete battery calculations for both the alarm and supervisory power requirements. Submit ampere-hour requirements for each system component with the calculations.

          - Complete riser diagrams indicating the wiring sequence of all new devices and their connections to the control equipment.  Provide a color code schedule for the wiring.  Provide floor plans showing the location of all devices and equipment.

      - AS-BUILT DRAWINGS

        - General:  Submit to the Contracting Officer 6 sets of detailed "as-built" drawings.  The drawings shall include complete wiring diagrams showing connections between all devices and equipment, both factory and field wired.  Include a riser diagram and drawings showing the as-built location of all devices and equipment.  The drawings shall show the system as installed, including all deviations from both the project drawings and the approved shop drawings.  The drawings shall also include all information as required by NFPA 72.  Submit the drawings on uniform-sized sheets not less than 30 by 42 inches.  Submit these drawings within two weeks after the final acceptance test of the system.

      - OPERATION AND MAINTENANCE MANUALS

        - General:  Not less than thirty days prior to the final acceptance testing of the entire system, and for use during the instruction period hereinafter specified, provide 6 bound copies of an operation and maintenance manual to the Contracting Officer.  The manual shall include an index, copies of all approved shop drawings and submittal materials (updated to as-built), and a complete parts list of all components.  The manual shall also include, for each item, the manufacturer's name, the serial number of the part, an ordering number, if appropriate, and a physical and electrical description of the part.  The manual shall also include a list of recommended spare parts.

        - Record Drawing Software: Provide one (1) set of CAD based drawings in DWG format of all as-built drawings and schematics.

      - INSTRUCTION OF GOVERNMENT EMPLOYEES

        - Due to the limited changes in programming, no instruction is required.

- PRODUCTS

      - ALARM INDICATING DEVICES

        - Fire Alarm Speakers: Provide fire alarm speakers conforming to UL 1480 having a minimum of four (4) tap settings and separate terminations for each "in" and "out" connection.  At a minimum, tap settings shall include taps of 1/4, ½, 1 and 2 watts.  Speakers shall be initially set at the 1/2 watt tap setting; however, setting shall be adjusted to meet sound pressure requirements.  Speakers shall have an output rating of 84 dBA at three (3) meters (9.9 feet) as determined by the reverberant room test; data on peak output as determined in an anechoic chamber is not suitable.  All speakers shall be capable of installation on standard 100 mm (4 inch) square electrical boxes.  Where speakers and strobes are provided in the same location, they may be combined into a single wall or wall/ceiling mounted unit.

- To ensure audible signals are clearly heard, the sound level shall be at least 70 dBA throughout the office spaces, courtrooms, general building areas and corridors measured 1.5 meters (5 feet) above the floor.  The sound level in other areas shall be at least 15 (fifteen) dBA above the average sound level or five (5) dBA above any noise source lasting 60 seconds or longer. Sound level measurements shall be taken with room doors closed.  Quantities of fire alarm speakers shown on the contract drawings are for cost estimating purposes only.  Additional speakers shall be provided at no additional expense to the government if the sound levels noted above are not achieved during the final acceptance testing.

        - Fire Alarm Strobes:  Provide visual alarm appliances (strobes) that operate on a supervised twenty-four (24) volt D.C. circuit.  The strobe lens shall comply with UL 1971 and conform to the Americans with Disabilities Act.  All strobes shall incorporate circuitry for synchronized strobe flash.  The strobe intensity shall have a minimum of four field selectable settings and shall be rated per UL Standard 1971 with a flash rate of one (1) flash per second minimum across the listed voltage range.  The strobes shall not drift out of synchronization at any time during operation.  The strobe shall have a Xenon flash tube.  The strobe shall have a red cover plate.

Provide synchronization modules on strobe light circuits, and/or synchronized power supplies, as necessary, to ensure strobe lights are synchronized in any vertical or horizontal line of sight, in accordance with NFPA 72

        - Combination Speaker/Strobe Units: Combination units may be used provided that the requirements in A. and B. are separately met for the speaker and strobe utilized in the combined unit.

- EXECUTION

      - SYSTEM FIELD WIRING

        - Wiring Within Cabinets, Enclosures, Boxes and Fittings: Provide wiring installed in a neat and workmanlike manner and installed parallel with or at right angles to the aides and back of any box, enclosure or cabinet.  All conductors that are terminated, spliced, or otherwise interrupted in any enclosure, cabinet, mounting or junction box shall be connected to terminal blocks.  Mark each terminal in accordance with the wiring diagrams of the system.  Make all connections with approved terminal blocks.

        - Alarm Wiring:  Provide minimum No. 16 AWG (use larger conductors where recommended by the fire alarm system or product manufacturers and/or if necessary to provide proper system operation and to avoid excessive voltage drops during operation) solid copper conductors with 600 volt 90 degrees C rated insulation in dry locations and 600 volt 75 degrees C insulation in wet or damp locations.  Provide wiring operating at 120 VAC as minimum No. 12 AWG solid copper having similar insulation. Install all conductors in rigid metal conduit or electrical-metallic tubing, utilizing compression type fittings and couplings, with a minimum diameter of 3/4 inches.  Run conduit or tubing concealed in finished areas unless specifically shown otherwise on the drawings.  Run conduit or tubing concealed unless specifically shown otherwise on the drawings.  All wiring for the fire alarm system must be installed in separate conduit.  No other building wiring is permitted in conduit that contains fire alarm wiring.  Pigtailing and "T-tapping" are not permitted.

        - Color Coding:  Color all wiring differently from the normal building wiring.  Use two different colors for alarm indicating circuits, for each type of initiating device circuit, and for each type of supervisory circuit.  The distinctive color code for each function shall remain the same throughout (e.g. changes in colors are not permitted).

      - FIRESTOPPING

        - General:  Firestop all holes for conduit, piping, or other penetrations which pass through floor slabs, fire-rated walls, partitions with fire-rated doors, vertical service shafts, or any fire-rated assemblies in accordance with Section 07270, Firestopping.

      - INSTALLATION

        - Alarm Indicating Devices:  Locate alarm indicating devices where shown on the drawings.  All devices shall be flush-mounted.

      - TESTS

        - Loop Resistance Tests:  Measure and record the resistance of each circuit with each pair of conductors in the circuit short-circuited at the farthest point from the circuit origin.  The tests shall be witnessed by the Contracting Officer and test results recorded for use at the final acceptance test.

        - Preliminary Testing:  Conduct preliminary tests to ensure that all devices and circuits are functioning properly.  Tests shall meet the requirements of Paragraph 3.5 of this section.  After preliminary testing is complete, provide a letter certifying that the installation is complete and fully operational.  The letter shall confirm that each initiating and indicating device was tested in place and functioned properly.  The letter shall also confirm that all panel functions were tested and operated properly.  The letter shall include the names and titles of the witnesses to the preliminary tests.   The contractor and the representative from each supplier of equipment shall be in attendance at the preliminary test to make necessary adjustments.  The Contracting Officer must be present at the preliminary test.

        - Final Testing:  Notify the Contracting Officer in writing when the system is ready for final acceptance testing.  Submit request to Contracting Officer for testing at least 15 calendar days prior to test date.  A final acceptance test will not be scheduled until operation and maintenance manuals have been received by the Contracting Officer.  Submit up-to-date redlined shop drawings to the Contracting Officer at the final test.  These drawings shall be undamaged sets of prints of the shop drawings, with changes from the original drawings marked in red.

The Contractor and an authorized representative from each supplier of equipment shall be in attendance at the final test.  The final test shall be witnessed by the authority having jurisdiction.  At the final test, any and all required tests shall be repeated at the discretion of the Government.

      - MINIMUM SYSTEM TESTS

        - General:  Test the system in accordance with the procedures outlined in NFPA 72.  The required tests are as follow:

          - Verify the absence of unwanted voltages between circuit conductors and ground.

          - Verify the control unit is in the normal condition as detailed in the manufacturer's operating and maintenance manual.

          - Test each initiating and indicating device and circuit for proper operation and response at the control unit.

          - Test the system for all specified functions in accordance with the contract's plan and specifications and the manufacturer's operating and maintenance manual.

          - Determine that the system is operable under trouble conditions as specified.

          - Visually inspect all wiring.

          - Verify that the alarms are audible throughout all areas of the renovated area.

          - Test 10 percent of initiating devices on other floors, as necessary, when required by NFPA 72.

      - SPARE PARTS AND TOOLS

        - Interchangeable Parts:  All spare parts furnished shall be directly interchangeable with the corresponding components of the installed system.  Spare parts shall be suitably packaged and identified by nameplate, tagging, or stamping.  Deliver spare parts to the construction engineer.

        - Spare Parts:  Provide the following spare parts and accessories:

2	Fire alarm speakers of each type installed.

2   	Fire alarm strobes of each type installed.

2	Combination fire alarm speaker/strobes of each type installed.

2	Sets of special tools required for the maintenance of the system.

        - Parts List:  Furnish a list, in duplicate, of all other parts and accessories that the manufacturer of the system recommends to be stocked for maintenance.

END OF SECTION