## FC922 & FC924
FC922/FC924 Battery Calc Sheet |  |  |  | Enter value
Version 1.2 |  |  |  | Select choice
Fixed
Ref. No. |  |  |  | Calculated
Submitted By:
Project Name: | Hilotn Garden Hotel
Project Location: | 145 Jetport Boulevard
Panel Location:
Node No: |  | Date:
Module | Description | Module Feature | Qty | Standby Current | Alarm Current
FCM2018-U3 | Standard Operating Unit |  | 1 | 0.125 | 0.125
FCM2019-U3 | Enhanced Operating Unit |  |  | 0 | 0
| With LED zones | LED zones
FCI2016-U1 | 252 pt Periphery Board |  | 1 | 0.11 | 0.11
|  | SLC load |  | 0.09564 | 0.09564 |  | Yes | No
|  | NAC load | 1 |  | 8
Aux power load
|  | Bell Follower | No | 0 | 0
FCI2017-U1 | 504 pt Periphery Board |  |  | 0 | 0
SLC load
NAC load
|  | Aux power load |  | 0 | 0
|  | Bell Follower | No | 0 | 0
FCI2011-U1 | NAC expander | yes | 1 | 0.015 | 0.015
NAC load
XCI2001-U1 | Releasing module | No | 0 | 0 | 0
Releasing load
FCI2020-U1 | City Tie/Leased Line module | Not Installed |  | 0 | 0 |  | Not Installed | Leased Line | City Tie
FN2001-A1 | SafeDLink Network module |  |  | 0 | 0
FCA2016-U1 | RS-485 module |  | 1 | 0.055 | 0.055
FN2006-U1 | Single-mode fiber module |  |  | 0 | 0
FN2007-U1 | Multi-mode fiber module |  |  | 0 | 0
FT2014-xx | Remote annunciator - display |  |  | 0 | 0
FT2015-xx | Remote annunciator - control |  | 1 | 0.034 | 0.034
FTI2001-A1 | Network terminal board |  |  | 0 | 0
FCM2023-U3 | LED expansion module |  |  | 0 | 0
|  | LED zones |  | 0 | 0
FCA2015-U1 | DACT |  | 1 | 0.025 | 0.025
FCA2018-U1 | Remote printer module |  |  | 0 | 0
Devices | Description | Qty | Stdby/Alm
HFP-11 / 8713 | Photo-thermal detector |  | 0 | 1.4 mA per device
HFPO-11 / 8710 | Photo detector |  | 0 | 1.4 mA per device
HFPT-11 / 8712 | Thermal detector |  | 0 | 1.4 mA per device
OOHC941 | Dual optical/thermal/CO detector |  | 0 | 0.75 mA per device
OOH941 | Dual optical/thermal detector | 6 | 0.00408 | 0.68 mA per device
OH921 | Photo-thermal detector | 65 | 0.0182 | 0.28 mA per device
OP921 | Photo detector | 65 | 0.0182 | 0.28 mA per device
HI921 | Thermal detector | 17 | 0.00476 | 0.28 mA per device
FDCIO422 | 4-input/4-output module | 7 | 0.007 | 1.0 mA per device
HMS / 8700-S-D-M | Manual station |  | 0 | 1.4 mA per device
HTRI-S / 8702 | Single input module | 25 | 0.035 | 1.4 mA per device
HTRI-D / 8703 | Dual input module | 3 | 0.0042 | 1.4 mA per device
HTRI-R / 8704 | Singl input/single relay module |  | 0 | 1.4 mA per device
HZM / 8705 | Conventional zone module |  | 0 | 1.4 mA per device
HCP / 8706 | Addressable control point | 3 | 0.0042 | 1.4 mA per device
ILED / 8726 | Intelligent LED |  | 0 | 1.4 mA per device
Total |  | 191 | 0.09564 | (included above) |  | System OK
Total Current |  |  |  | 0.45964 | 8.4596 | Use 300W power supply
Standby Time (hrs) |  |  | 24 | 11.0314 |  |  | 4 | 24 | 60 | 96
Alarm Time (min) |  |  | 5 |  | 0.70497 |  | 5 | 15 | 30
AH required (no reserve) |  |  |  |  | 11.7363
Battery Reserve |  |  | 125% |  |  |  | 110% | 120% | 125%
AH Required (with reserve) |  |  |  |  | 14.6704 | System OK
| Battery Size Provided | 18 | AH
Note on D17: Indicated the number of NACs used on this periphery board
Note on D22: Indicated the number of NACs used on this periphery board
Note on C18: Do not include aux power for Network Annunciators or Remote Annunciators - they are included elsewhere
Note on C23: Do not include aux power for Network Annunciators or Remote Annunciators - they are included elsewhere
Note on B31: Required for remote annunciator and remote printer module - max 8 per RS-485
Note on B40: Requires an RS-485 module
Note on B34: Requires an RS-485 module
Note on B35: Requires an RS-485 module
Note on A43: Requires 1.4 mA per device
Note on A44: Requires 1.4 mA per device
Note on A45: Requires 1.4 mA per device
Note on A52: Requires 1.4 mA per device
Note on A53: Requires 1.4 mA per device
Note on A54: Requires 1.4 mA per device
Note on A55: Requires 1.4 mA per device
Note on A56: Requires 1.4 mA per device
Note on A57: Requires 1.4 mA per device
Note on A58: Requires 1.4 mA per device
Note on A46: Requires 0.75 mA per device
Note on A47: Requires 0.68 mA per device
Note on A48: Requires 0.28 mA per device
Note on A49: Requires .28 mA per device
Note on A50: Requires 0.28 mA per device
Note on A51: Requires 1 mA per device
Note on A27: The system supports EITHER a NAC expander or a releasing module - not both!
Note on D12: Include Operating Units in Network terminals powered from this panel
Note on D13: Include Operating Units in Network terminals powered from this panel
Note on A20: Only 1 periphery board per system supported!
Note on B36: Needed for every Operating Unit in a Network Terminal
Note on D26: Indicated the number of NACs used on this expander board
Note on F17: Include the TOTAL NAC power for this board
Note on F22: Include the TOTAL NAC power for this board
Note on F26: Include the TOTAL NAC power for this board
Note on D28: Indicated the number of releasing circuits used on this board
Note on F28: Include the TOTAL releasing power for this board