05P225

TO:       	Jean Fraser – Planner

FROM:  	Jim Seymour – Development Review Coordinator, Sebago Technics, Inc.

# RE:       	Major Site Plan Review:  41 Hutchins Drive, Woodard & Curran Expansion

# DATE:   	January 31, 2006

Sebago Technics has reviewed the revised submittal of the Major Site Plan application and supporting documentation with latest revision dated January 20, 2006 for the proposed expansion of their current office complex located at 41 Hutchins Drive in the City of Portland. It is our understanding that this development is on a lot, which was part of the Stroudwater Estates Subdivision, which obtained approval of a Maine DEP Site Location of Development permit in the 1980’s. Since this site has not reached a threshold of 3 acres impervious it has not triggered a separate requirement for a Site Location permit based on current DEP standards. We respectfully offer the following comments in outline format:

1.	Stormwater Management

Review of the stormwater management plan and subsequent runoff quantity and quality calculations were in a state of flux with the recent transition of the new Chapter 500: Stormwater Management Law and given the City was relieved of its delegated review authority, both the MeDEP and the City of Portland were not clear on the review level required for this site (quantity vs. quality).  We discussed a strategy to address concerns of treatment vs. detention for dealing with stormwater management plan with which staff and the Planning Board could support for approval.

A. 	The project will shows evidence that they meet the stormwater quality and quantity standard as required by the City’s stormwater standard for required treatment when parking areas exceed 25 spaces. The narrative and calculations discussing and showing proof that the standard was submitted for the entire site. Recent meetings disclosed that the previous DEP order required quantity control. The applicant has shown that the peak rate from runoff has been met for the entire site, through detainment measures such as detention and infiltration ponds.

Our review of the quality calculations revealed that the treatment factors utilized for wooded buffer treatment appear not to be correctly sized and incorporate the use of wetlands, which are not allowed. This affects the overall treatment value, which may reduce the effective sediment removal and not meet the sliding scale factor as declared by the engineer. The engineer must re-evaluate the treatment factors for our or staff review.

As attempted all buffers shall be shown on the site plan with labels indicating the width, slope, and percentage of removal efficiency for each buffer shown.

B. 	All structures such as manholes, catch basins, and drainage structures with surface openings must label rim elevations.

C.	The curbing along the access driveway/road along the addition should be extended to discourage scouring at the pavement edge. Therefore, we recommend curbing be extended to the edge of sidewalks at the entrance. The curbing from the building’s end sidewalk shall be extended from the circle as well.

D.	The internal parking lot islands must be curbed in the satellite lot, for protection of landscape features.

E.	Will the underground detention/storage require an underdrain due to the depth in poor clay silt soils where water tables could be high?

2.	Road Access/Circulation

A.	Please refer to comments from the City Traffic Engineer for concerns of traffic movements, trip generation, and internal movements.

B. 	The access lanes per driveway standards are required to be 24 feet for two-way access. The applicant has requested a waiver of the standard because of the limitations of the wetlands, which traverse the site. The claim is that any further extension of the fill for the road widening will create difficulties in permitting and unnecessary impacts to the wetlands. The proposed road is 20 feet wide with guardrails on the wetland side and a 5-foot grass esplanade against the building.

Typically, the waiver requests for driveway/aisle widths have occurred with City Infill Sites where property limitations and building structures have a physical and geometrical impact on the redevelopment proposed. This property is unique in that the development and the wetland restraint is a direct result of the actions taken by the developer/applicant. The building size, configuration, parking layout, and expansion planning was determined by the applicant. Property lines and existing buildings are not the restriction, but a natural resource is.

The width of 20 feet is marginal, and it is clear 24 feet width is desirable. Based on the layout and spacing between the proposed structure we feel 22 feet may be completed with a compromise of 1 foot towards the building and 1 foot towards the wetlands, with the access road from the proposed building’s Hutchins Drive end to the curb cut designed to be 24 feet not 22 feet.  Final discussion, arguments, and impacts will have to be weighed by the Board. Our feeling is that at a minimum, both the City and applicant, to accomplish and improvement for safety and vehicular passage can make a compromise for a 22-foot road.

C.	Details are needed for the sidewalk section along the street frontage and shall be in accordance with City of Portland design standards.

3.	Utilities

A.	Letters to serve and available capacities have been requested showing that adequate service exists for the development. To date those have not been administered by Public Works

B.	The City wastewater division and City Engineer shall assist review of the construction details and location of the re-located interceptor sewer. We did not receive plans or construction details for the sewer relocation plan or profile design. All designs must be in accordance with City details, and the City must accept relocated easements. This should be directly reviewed by Public Works, but we can assist is so directed.

C.	There is a 12 inch steel culvert shown outleting into the stream from either Hutchins Drive or the Water District easement. Please place an easement around this drainage pipe such that either the City or Water District has rights to maintain on private property.

4.	Grading & Erosion Controls

A.	The applicant should consider stabilized entrances when building the parking lots and access drives. Notes shall be added addressing mud tracking, pavement cleaning, dust control, and or street sweeping during construction.

B.	All existing and proposed catch basins in or near the construction area shall be protected with Silt sacs until the base course of paving is completed for the project.

5.	General

A.	The project has an attached Geotechnical report, which shall be adhered to during construction. The plans shall add a note referencing the construction measures required for such foundation and retaining wall construction. The final retaining wall design shall be designed by a profession engineer, and reviewed and approved by the code enforcement officer. It also may be beneficial to require weekly reports from a geotechnical engineer or geologist summarizing findings and construction monitoring during excavation and preparation of the retaining walls and building foundations.

B.	The applicant is likely required to file a revised Maine Construction General Permit for this project.  This must be obtained prior to the start of construction.  Additionally the applicant shall indicate on the drawings a construction elevation benchmark with the datum specified. Ideally this should be in accordance with City datum for sewer project work. Please contact Bill Clark at public Works to confirm Survey information requirements.

C. 	The applicant has appears to have available space for development, but given resource protection limits, treatment measures requiring avoidance of snow storage, and given the extent of parking, snow removal is of some concern. Please provide on a plan to address snow storage locations on site or note on the site plan how it will be removed.

Overall, the project has addressed many challenges.  However, the applicant should make the necessary revisions, as noted in the above comments to conform to City stormwater treatment issues for water quality, and some minor grading and parking layout/aisle concerns. If the board determines that the items left can be agreed to, and will be completed by the applicant, we can support conditional approval for the project

Please contact our office if you have any questions.

JRS/jrs