## MS-9200UDLS
MS-9200UDLS Rev.3 Battery Calculation
Secondary Power Source Requirements | [10 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[11 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) |  |  |  |  | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total | 20 Minutes | 0.334 | 72 Hours | 72
Main Circuit Board | 1 | x | 0.137 | = | 0.137 | 1 | x | 0.36 | = | 0.36 | 25 Minutes | 0.417 | 90 Hours | 90
XRM-24B | 0 | x | 0 | = |  | 0 | x | 0 | = |  | 30 Minutes | 0.5
4XTMF | 0 | x | 0.005 | = |  | 0 | x | 0.011 | = |  | 45 Minutes | 0.75
IPDACT-2 | 0 | x | 0.093 | = |  | 0 | x | 0.136 | = |  | 60 Minutes | 1
IPDACT-2UD | 0 | x | 0.098 | = |  | 0 | x | 0.155 | = |  | 90 Minutes | 1.5
ANN-BUS Devices | [10 empty] | 120 Minutes | 2
ANN-80 | 1 | x | 0.015 | = | 0.015 | 1 | x | 0.04 | = | 0.04 | 180 Minutes | 3
ANN-80-W | 0 | x | 0.015 | = |  | 0 | x | 0.04 | = |  | 240 minutes | 4
ANN-LED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
ANN-RLED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
ANN-RLY | 0 | x | 0.015 | = |  | 0 | x | 0.075 | =
ANN-I/O | 0 | x | 0.035 | = |  | 0 | x | 0.2 | =
ANN-I/O LED | 0 | x | 0 | = |  | 0 | x | 0.01 | =
ANN-S/PG | 0 | x | 0.045 | = |  | 0 | x | 0.045 | =
ACS Annunciators
ACM-8RF | 0 | x | 0.03 | = |  | 0 | x | 0.158 | =
ACM-16ATF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
ACM-32AF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
AEM-16ATF | 0 | x | 0.002 | = |  | 0 | x | 0.018 | =
AEM-32AF | 0 | x | 0.002 | = |  | 0 | x | 0.018 | =
AFM-16ATF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
AFM-32AF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
AFM-16AF | 0 | x | 0.025 | = |  | 0 | x | 0.065 | =
LDM-32F | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
LDM-E32F | 0 | x | 0.002 | = |  | 0 | x | 0.018 | =
LCD-80F | 0 | x | 0.025 | = |  | 0 | x | 0.064 | =
Conventional Detectors | 0 | x | 0 | = |  | 0 | x | 0 | =
EOLR-1 | 0 | x | 0.02 | = |  | 0 | x | 0.02 | =
Addressable Devices
BEAM355 | 0 | x | 0.002 | =
BEAM355S | 0 | x | 0.002 | =
BEAM1224 | 0 | x | 0.017 | =
CP355 | 0 | x | 0.0003 | =
SD355 | 2 | x | 0.0003 | = | 0.0006
SD355T | 0 | x | 0.0003 | =
AD355 | 0 | x | 0.0003 | =
H355 | 1 | x | 0.0003 | = | 0.0003
H355R | 0 | x | 0.0003 | =
H355HT | 0 | x | 0.0003 | =
D350P | 0 | x | 0.0003 | =
D350RP | 0 | x | 0.0003 | =
D350PL | 0 | x | 0.0003 | =
D350RPL | 0 | x | 0.0003 | =
D355PL | 0 | x | 0.0003 | =
MMF-300 | 5 | x | 0.0004 | = | 0.002
MMF-300-10 | 0 | x | 0.0035 | =
MDF-300 | 0 | x | 0.00075 | =
MMF-301 | 0 | x | 0.000375 | =
MMF-302 | 0 | x | 0.00027 | =
MMF-302-6 | 0 | x | 0.002 | =
BG-12LX | 3 | x | 0.00023 | = | 0.00069
CMF-300 | 0 | x | 0.00039 | =
CMF-300-6 | 0 | x | 0.00225 | =
CRF-300 | 0 | x | 0.00027 | =
CRF-300-6 | 0 | x | 0.00145 | =
I300 | 0 | x | 0.0004 | =
B501BH-2 | 0 | x | 0.001 | =
B501BHT-2 | 0 | x | 0.001 | =
B200SR | 0 | x | 0.0005 | =
B224RB | 0 | x | 0.0005 | =
B224BI | 0 | x | 0.00045 | =
| Maximum alarm draw for all Addressable devices ---------------> | [8 empty] | 0.4
CMF-300 (Aux. Power) | 0 | x | 0.0017 | = |  | 0 | x | 0.007 | =
CMF-300-6 (Aux. Power) | 0 | x | 0.008 | = |  | 0 | x | 0.02 | =
MMF-302 (Aux. Power) | 0 | x | 0.012 | = |  | 0 | x | 0.09 | =
MMF-302-6 (Aux. Power) | 0 | x | 0.05 | = |  | 0 | x | 0.27 | =
B200SR (Aux. Power) | 0 | x | 0.0005 | = |  | 0 | x | 0.035 | =
Miscellaneous Device 1 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 2 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 3 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 4 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 5 | 0 | x | 0 | = |  | 0 | x | 0 | =
NAC 1 |  |  | 0 | = |  |  |  | 1.439 | = | 1.439
NAC 2 |  |  | 0 | = |  |  |  | 0 | =
NAC 3 |  |  | 0 | = |  |  |  | 0 | =
NAC 4 |  |  | 0 | = |  |  |  | 0 | =
Resettable 1 |  |  | 0 | = |  |  |  | 0 | =
Non-Resettable 1 |  |  | 0 | = |  |  |  | 0 | =
Total Standby Load |  |  |  |  | 0.15559 | Total Alarm Load |  |  |  | 2.239
MS-9200UDLS Rev.3 Battery Calculation
Note 1: You are fully responsible for verifying these calculations.
Note 2: Use the dropdowns in the yellow cells to enter values.
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current |  |  | 0.15559 |  |  | x | 24 |  | = | 3.7342
Required Alarm Time in Minutes
5 Minutes
Alarm Load Current (Amps) |  |  | 2.239 |  |  | x | 0.084 |  | = | 0.18808
Total Current Load | [9 empty] | 3.9222
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 4.7067
Recommended Batteries: | [5 empty] | BAT-1270 - 7AH Batteries
Battery Check
The batteries can be charged by the MS-9200UDLS Charger.
The batteries can be housed in the MS-9200UDLS Cabinet.
Current Draw Check
NAC#1 current is within the limitations of the circuit.
NAC#2 current is within the limitations of the circuit.
NAC#3 current is within the limitations of the circuit.
NAC#4 current is within the limitations of the circuit.
MS 9200UDLS Control Panel:
The output current is within the panel's limitations.
MS-9200UDLS Rev.3 Circuit Detail
NAC 1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
P2R @ 75 Candela | 3 | x | 0 | = | 0 | 3 | x | 0.176 | = | 0.528
P2R @ 30 Candela | 1 | x | 0 | = | 0 | 1 | x | 0.116 | = | 0.116
P2R @ 110 Candela | 3 | x | 0 | = | 0 | 3 | x | 0.221 | = | 0.663
SR @ 15 Candela | 2 | x | 0 | = | 0 | 2 | x | 0.066 | = | 0.132
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 1.439
NAC 2
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 3
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
NAC 4
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
Resettable 1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0 | Total Alarm Load |  |  |  | 0
Non-Resettable 1
Device | Qty | Non-Alarm Draw |  |  | Total | Qty | Alarm Draw |  |  | Total
ANN-80 | 1 | x | 0.015 | = | 0.015 | 1 | x | 0.04 | = | 0.04
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
| 0 | x | 0 | = |  | 0 | x | 0 | =
Total Standby Load |  |  |  |  | 0.015 | Total Alarm Load |  |  |  | 0.04
Note on H95: Select Standby Time in Hours from the dropdown list.
Note on H98: Select the Alarm Time in minutes from the dropdown list.
Note on H101: Select the Derating Factor from the dropdown list.