**8.7.17 – 12-17 BISHOP ST.- PINETREE RECOVERY CODE REVIEW SUMMARY**

**Project Description;**

**12-17 Bishop Street is a two story wood framed structure with wood framed floor and roof. The wood frame is protected at floors and walls with 5/8” sheetrock. 12 Bishop is the parking lot, 17 Bishop is the building site. The building has 12,100 total s.f., (approximately 6,000 s.f. per floor) that is currently partitioned into rooms and spaces that suite this tenant well. Pinetree Recovery will have 20 clients and additional staff as well as upper floor administrative space.**

**Site:**

**We are considering minimal work at the moment. Replacement of asphalt with crushed stone and a planted screen are proposed at the rear of the property. The parking lot across the street accommodates 25 cars.**

**Portland Zoning- 2009- Relevant sections;**

**14-250 Dimensional Req.:**

**I-M zone- permitted use, day program and intermediate care facility**

**Existing lot size- .56 ac.**

**Setback requirements – NO EXPANSION PLANNED**

 **Street frontage Existing to remain**

 **Front setback- Existing to remain**

 **Side setback- Existing to remain**

 **Rear yard- varies, existing to remain**

**Parking- one space for every 5 beds @ intermediate care, one space per 400 s.f. of area for day program. The program will have 20 clients and 18 staff. Clients are not permitted to have cars, but the staff will. We propose to “right size” our parking requirement at about 20 cars. We have access to 25 spaces with the current plan.**

**Max. permitted imperv. surface –90% for B2 zone. NO ADDITIONAL PAVING PROPOSED**

**Max. permitted bldg. height - Existing two story height to remain**

**Paved Parking Area- Existing parking area to remain.**

**Lighting- Existing exterior lighting to remain.**

**Signage-Signage will be applied to the glass entry vestibule at the main building entry.**

**Trash- Trash will be handled with a dumpster and waste contracting service.**

**IBC- 2009- Relevant sections;**

**The existing building use is defined as R-1 Board and Care .**

**Per table 503 the existing, sprinkled Type V B/ R-1 (SM) structure can have 21,000 s.f. per floor and be 2 stories. We are 12,000 s.f. per floor, 2 stories, protected and fully sprinkled**

**Fire Department checklist- please refer to plan for travel distance, F.E. locations, notification, emergency lighting, exit signs, etc.**

**EXISTING KNOX BOX AT ENTRY SHALL REMAIN**

1. Owner- **Pinetree Recovery- Justin Barrett**

 2. Architect- **Whipple Callender Architects, PO Box 1276 Portland, Maine 04101 (775-2696)**

3. Proposed use- **Board and Care facility**

 4. Square footage of structure- **12,100 s.f. gross (+/- 6,000 s.f. / flr.)**

 5. Elevation of all structures**- existing 10’ floor to floor**

 6. Proposed fire protection of all structures- **fully sprinkled**

7. Hydrant Locations- **Bishop St.**

 8. Water main sizes and locations- **not known**

 9. Access to any Fire Department Connections-**Connection to existing sprinkler system provided**

10. Access to all structures (2 sides Min.)- **Clear access to 3 sides**

11. A code summary shall be included referencing NFPA and all fire department technical standards-

**NFPA 101-2009 – Chapter 32: New Residential Board and Care**

**32.1 General Requirements**

**32.1.1.3 Chapter Sections.**

**(3) Section 32.3. Large Facilities (that is, sleeping accommodations for more than 16 residents)- WE ANTICIPATE 20 CLIENTS FOR THE DETOX FACILITY. CHANGE IN UPSTAIRS USE WILL REQUIRE PERMITTING AND REVIEW FOR THAT PART OF THE WORK.**

**32.1.2 Multiple Occupancies- N.A. - BOTH FLOORS WILL BE OCCUPIED BY THE SAME TENANT**

**32.3 Large Facilities.**

**32.3.1.3 Minimum Construction Requirements. Large Board and Care facilities shall be limited to the building construction types in Table 32.3.1.3 based on the number of stories in height. AS TYPE V(111) WE ARE PERMITTED TO BE A TWO STORY OCCUPANCY**

**32.3.1.4 Occupant Load. WE ANTICIPATE UP TO 20 CLIENTS AND ADDITIONAL STAFF FOR THIS PHASE OF WORK**

**32.3.2 Means of Egress.**

**32.3.2.1.1 Means of egress from resident rooms and resident living units shall be in accordance with Chapter 7 and this chapter.**

**32.3.2.2.2 Doors. Doors in means of egress shall be as follows: REFER TO DOOR SCHEDULE**

1. **Doors complying with 7.2.1 shall be permitted**
2. **Doors within individual rooms or suites of rooms shall be permitted to be swinging or sliding.**
3. **No door shall be equipped with a lock requiring a tool or key from the egress side.**
4. **Delayed egress locks in accordance with 7.2.1.6.1 shall be permitted , provided not more than 1 device is located in any egress path.**
5. **Access controlled egress doors in accordance with 7.2.1.6.2 shall be permitted.**
6. **6. Doors located in the means of egress are permitted to be locked under the provisions of Chapter 32 #4 & #5, shall have adequate provisions made for rapid removal of occupants by means such as remote control of locks, keying of locks to keys carried by staff at all times, or other such reliable means available to staff at all times.**
7. **Only one such locking device described in #6 shall be permitted at each door.**

**32.2.2.3 Stairs**

**32.2.2.3.1 Stairs complying with 7.2.2 shall be permitted. EXISTING STAIRS COMPLY**

**32.3.2.3 Capacity of Means of Egress**

**32.3.2.3.3 The width of corridors shall be sufficient for the occupant load served and but shall not be less than 60”. 5’ WIDE CORRIDORS SHALL BE PROVIDED**

**32.3.2.4 Number of Exits. The minimum number of exits as required by Section 7.4 shall be provided on every story. TWO MEANS OF EGRESS ARE PROVIDED AT EACH FLOOR.**

**32.3.2.5 Arrangement of Means of Egress**

**32.3.2.5.1 Access to all required exits shall be in accordance with Section 7.5. WE COMPLY WITH SECTION 7.5**

**32.3.2.6 Travel Distance to Exits. Travel distance from any point in a room to the nearest exit, measured in accordance with Section 7.6, shall not exceed 250 ft.- 156 ‘ TRAVEL DISTANCE IS LESS THAN 250 FT., PLEASE REFER TO FLOOR PLAN**

**32.3.2.9 Emergency Lighting. Emergency lighting in accordance with Section 7.9 shall be provided unless each sleeping room has direct exit to outside at finished ground level. WE WILL PROVIDE EMERGENCY LIGHTING PER SECTION 7.9**

**TABLE 32.3.3.2.2 Hazardous area protection. WE WILL PROVIDE PROTECTION IN AREAS NOTED IN THE SEPARATION TABLE**

**32.3.2.3 Means of egress from resident rooms and resident living units shall be in accordance with Chapter 7 and this chapter.**

**31.3.3.3.2 Interior wall and ceiling finish. Interior finishes shall comply with Section 10.2 and be in accordance with the following:**

**1. Exit Enclosures-Class A**

**2. Lobbies and Corridors-Class B**

**3. Rooms and Enclosed Spaces – Class B**

**WE WILL COMPLY WITH THESE REQUIREMENTS**

**32.3.3.4 Detection, Alarm and Communication Systems**

**32.3.3.4.2 Initiation. The required fire alarm system shall be initiated by the following:**

**1. Manual means in accordance with 9.6.2**

**2. Manual fire box located at a convenient central control point under continuous supervision of responsible employees.**

**3. Required sprinkler system.**

**4. Required detection system.**

**ALL 4 INITIATION ITEMS WILL BE PROVIDED**

**32.3.3.4.3 Annunciator panel. An annunciator panel, connected to the fire alarm system,shall be provided at a location readily accessible from the primary point of entry for emergency response personnel. ANNUNCIATOR PANEL WILL BE PROVIDED. PANEL DESIGN SHALL BE APPROVED BY THE STATE FIRE MARSHALL.**

**32.3.3.4.4 Occupant notification. Occupant notification shall be provided automatically, without delay in accordance with 9.6.3. WE WILL PROVIDE OCCUPANT NOTIFICATION.**

**32.3.3.4.6 Emergency Forces Notification. Emergency forces notification shall meet the following requirements:**

**1. Fire Dept. notification shall be in accordance with 9.6.4**

**2. moke detection (systems) shall be permitted to initiate primary alarm system in accordance with 9.6.3.4 for not more than 120 seconds.**

**WE WILL PROVIDE EMERG. FORCES NOTIFICATION.**

**32.3.3.4.8 Smoke Detection Systems.**

**32.3.3.4.8 Corridors and spaces open to corridors, other than those meeting the requirements of 32.3.3.4.8.3 shall be provided with smoke detectors that comply with NFPA 72 National fire Alarm Code and are arranged to initiate an alarm that is audible in all sleeping areas. WE WILL PROVIDE CORRIDOR SMOKES THAT INITIATE SLEEPING AREA ALARMS**

**32.3.3.5 Extinguishing requirements**

**32.3.3.5.1 General. All buildings shall be protected throughout by an approved automatic sprinkler system installed in accordance with 9.7.1.1 (1) . THE BUILDING IS SPRINKLED WITH AN EXISTING SUPERVISED & MONITORED SPRINKLER SYSTEM COVERING THE ENTIRE BUILDING.**

**32.3.3.5.6 Portable Fire Extinguishers. Portable fire extinguishers shall be provided in accordance with 9.7.4.1. FIRE EXTINGUISHERS WILL BE PROVIDED**

**32.3.3.6 Corridors and Separation of Sleeping Rooms.**

**32.3.3.6.2 Sleeping Room shall be separated from corridors, living areas and kitchens by walls complying with 32.3.3.6.3 through 32.3.3.6.6 WE WILL COMPLY WITH REQUIREMENTS**

**32.3.3.6.3 Walls required by 32.3.3.6.1 through 32.3.3.6.2 shall be smoke partitions in accordance with Section 8.4 having a minimum ½ hr. fir resistance rating. 1 HR. WALLS WILL BE PROVIDED**

**32.3.3.6.4 Doors protecting corridor openings shall not be required to have a fire protection rating but shall but shall be constructed to resist the passage of smoke. DOORS WILL FIT FRAMES AND NOT BE OVERCUT AT THE SILL**

**32.3.3.6.5 Door closing devices shall not be required on doors in corridor wall openings, other than those serving exit enclosures, smoke barriers, enclosures of vertical openings and hazardous areas. REFER TO DOOR SCHEDULE FOR DOORS WITH CLOSERS.**

**32.3.3.6.6 No louvers, grilles, operable transom, other than properly installed heating and utility installations shall penetrate the walls of doors specified in 32.3.3.6 NO GRILLES ARE PLANNED FOR INTERIOR DOORS**

**32.3.3.7 Buildings shall be subdivided by smoke barriers in accordance with 32.3.3.7.1 through 32.3.3.7.21- REFER TO PLAN FOR PROPOSED SMOKE BARRIER LOCATIONS AT EACH FLOOR**

**32.3.3.7.1 Every story shall be divided into not less than two smoke compartments, unless it meets the requirements of 32.3.3.7.4, 32.3.3.7.5, 32.3.3.7.6, 32.3.3.7.7. PLEASE REFER TO FLOR PLANS FOR SMOKE BARRIER LOCATIONS ON UPPER AND LOWER FLOORS**

**32.3.3.7.2 Each smoke compartment shall have an area not exceeding 22,500 s.f. OK THE 6,000 S.F. PLOOR PLATE WILL BE ROUGHLY DIVIDED IN HALF.**

**32.3.3.7.3 The travel distance from any point to reach a door in the required smoke barrier shall be limited to a distance of 200 ft. DISTANCE IS LESS THAN 200 S.F.**

**32.3.3.7.4 Smoke barriers shall not be required on stories that do not contain a board and care facility located above the board and care facility. WE PLAN ON INSTALLING A SMOKE BARRIER AT FLOOR TWO.**

**32.3.3.7.5 Smoke barriers shall not be required in areas that do not contain a board and care occupancy and that are separated from the board and care occupancy by a fire barrier complying with Section 8.3**

**32.3.3.7.8 Smoke barriers shall be constructed in accordance with Section 8.5 and shall have a minimum 1 hr. fire resistance rating unless they meet the requirements of 32.3.3.7.9 or 32.3.7.10. BARRIER WILL HAVE A 1 HR. FIRE RATING**

**32.3.3.7.10 Dampers shall not be required in duct penetrations of smoke barriers in fully ducted heating, ventilating and air conditioning systems. NO DAMPERS REQUIRED, WE ARE FULLY DUCTED.**

**32.3.3.7.11 Not less than 15 net s.f. shall be provided for each resident within the aggregate area of corridors, lounge or dining areas and other low hazard areas on each side of the smoke barrier. WE MEET THIS REQUIREMENT**

**32.3.3.7.13 Doors in smoke barriers shall be substantial doors, such as 1 ¾” thick solid core doors or shall be of construction that resists the fire for a minimum of 20 minutes. DOORS WILL BE SOLID CORE, NO VISION PANELS ON MAGNETIC HOLD OPENS TIED TO THE NEW FIRE ALARM.**

**32.3.3.7.16 Swinging doors shall be arranged so that each door swings in a direction opposite from the other.**

**32.3.3.7.17 Doors in smoke barriers shall comply with 8.5.4 and shall be self closing or automatic closing in accordance with 7.2.1.8. REFER TO DOOR SCHEDULE**

**32.3.3.7.19 Rabbets, bevels, or astragals shall be required at the meeting edges, and stops shall be required at the head and sides of doors and frames in smoke barriers.**

**32.3.3.7.20 Positive latching hardware shall not be required. LATCH NOT PROVIDED AT SMOKE BARRIER.**

**32.3.3.7.21. Center mullions shall be prohibited.**

**32.3.3.8 Cooking Facilities. Cooking facilities, other than those within indiv. residential units, shall be protected in accordance with 9.2.3 THE NEW COOKING FACILITIES WILL MEET THE REQUIREMENTS OF 9.2.3**

**32.7.1 Emergency Plan- WILL BE PROVIDED AND POSTED**

**32.7.2 Resident Training- WILL BE MANAGED BY STAFF**

**32.7.3 Emergency Egress and Relocation Drills -WILL BE MANAGED BY STAFF**