|  | Form Completion Date: |  | Supplemental Pages Attached: |  |  |
| --- | --- | --- | --- | --- | --- |

1.	Property Information

| Name of property: | 429 Warren Avenue Building |
| --- | --- |
| Address: | 429 Warren Avenue Building |
| Description of property: | Multi-unit commercial space |
| Name of property representative: | Knox Electric |
| Address: |  |
| Phone: |  | Fax: |  | E-mail: |  |

2.	INSTALLATION, SERVICE, TESTING, AND MONITORING INFORMATION

| This ONLY pertains to the installation and testing of the 2 added notification devices in the unit (one visual in bathroom, one hornstrobe mid hall), it does not constitute a full system test or inspection, this system and account belong to another vendor. Installation contractor: |  |
| --- | --- |
| Address: | Protection Professionals 325 US Route 1 Falmouth ME |
| Phone: | 207-775-5755 | Fax: |  | E-mail: | mail@protectionprofessionals.net |
| Service organization: | PROTECTION PROFESSIONALS |
| Address: | 325 US ROUTE 1 FALMOUTH, ME 04105 |
| Phone: | 207-775-5755 | Fax: | 207-781-2064 | E-mail: | mail@protectionprofessionals.net |
| Testing organization: | PROTECTION PROFESSIONALS |
| Address: | 325 US ROUTE 1 FALMOUTH, ME 04105 |
| Phone: | 207-775-5755 | Fax: | 207-781-2064 | E-mail: | Mail@protectionprofessionals.net |
| Effective date for test and inspection contract: |  |
| Monitoring organization: | Existing |
| Address: |  |
| Phone: |  | Fax: |  | E-mail: |  |
| Account number: |  | Phone line 1: |  | Phone line 2: |  |
| Means of transmission |  |
| Entity to which alarms are retransmitted: |  | Phone: |  |

3.	DOCUMENTATION

| On-site location of the required record documents and site-specific software: |  |
| --- | --- |

4.	DESCRIPTION OF SYSTEM OR SERVICE

| This is a: | New system | Modification to existing system | Permit number: |  |
| --- | --- | --- | --- | --- |
| NFPA 72 edition: | 2013 |  |
| 4.1 Control Unit |
| Manufacturer: | Existing | Model number: | Existing |
| 4.2 Software and Firmware |
| Firmware revision number: | Existing |

| 4.3 Alarm Verification | This system does not incorporate alarm verification. |
| --- | --- |
| Number of devices subject to alarm verification: |  | Alarm verification set for |  | seconds |

5.	SYSTEM POWER

| 5.1 Control Unit |
| --- |
| 5.1.1 Primary Power |
| Input voltage of control panel: | 120VAC | Control panel amps: | Existing |
| Overcurrent protection: Type: | Existing | Amps: | Existing |
| Branch circuit disconnecting means location: | Existing | Number: | Existing |
| 5.1.2 Secondary Power |
| Type of secondary power: | SLA Batteries |
| Location, if remote from the plant: | In Panel |
| Calculated capacity of secondary power to drive the system: |
| In standby mode (hours): | 24HRS | In alarm mode (minutes): | 5MIN |
| 5.2 Control Unit |
| This system does not have power extender panels |
| Power extender panels are listed on supplementary sheet A |

6.	CIRCUITS AND PATHWAYS

| Pathway Type | Dual Media Pathway | Separate Pathway | Class | Survivability Level |
| --- | --- | --- | --- | --- |
| Signaling Line | NA | NA | B | 0 |
| Device Power | NA | NA | NA | NA |
| Initiating Device | NA | NA | NA | NA |
| Notification Appliance | NA | NA | B | 0 |
| Other (specify): | NA | NA | NA | NA |
| NA |  |  |  |  |

7.	REMOTE ANNUNCIATORS

| Type | Location |
| --- | --- |
| Existing |  |
| NA | NA |

8.	INITIATING DEVICES

| Type | Quantity | Addressable or Conventional | Alarm or Supervisory | Sensing Technology |
| --- | --- | --- | --- | --- |
| Manual Pull Stations | NA | ADDRESSABLE | ALARM | CONTACT |
| Smoke Detectors | NA | ADDRESSABLE | ALARM | PHOTOELECTRIC |
| Duct Smoke Detectors | NA | NA | NA | NA |
| Heat Detectors | NA | NA | NA | NA |
| Gas Detectors | NA | ADDRESSABLE | Gas Supervisory | CO |
| Waterflow Switches | NA | ADDRESSABLE | ALARM | CONTACT |
| Tamper Switches | NA | ADDRESSABLE | SUPERVISORY | CONTACT |

9.	NOTIFICATION APPLIANCES

| Type | Quantity | Description |
| --- | --- | --- |
| Audible | NA | NA |
| Visible | 1 | Strobes |
| Combination Audible and Visible | 1 | Horn Strobes |

10.	  SYSTEM CONTROL FUNCTIONS

| Type | Quantity |
| --- | --- |
| Hold-Open Door Releasing Devices | NA |
| HVAC Shutdown | NA |
| Fire/Smoke Dampers | NA |
| Door Unlocking | NA |
| Elevator Recall | NA |
| Elevator Shunt Trip | NA |
| NA | NA |
| NA | NA |

11.	  INTERCONNECTED SYSTEMS

| This system does not have interconnected systems. |
| --- |
| Interconnected systems are listed on supplementary sheet | NA | . |  |

12.	  CERTIFICATION AND APPROVALS

| 12.1 System Installation Contractor |
| --- |
| This system as specified herein has been installed according to all NFPA standards cited herein. |
| Signed: | Devon H Bertin | Printed name: | Devon Bertin | Date: | 2/7/19 |
| Organization: | Protection Professionals | Title: | Tech | Phone: | 207-775-5755 |
| The above ONLY pertains to the installation and testing of the 2 added notification devices in the unit, it does not constitute a full system test or inspection, this system and account belong to another vendor. |
| 12.2 System Operational Test |
| This system as specified herein has tested according to all NFPA standards cited herein. |
| Signed: | Devon H Bertin | Printed name: | Devon Bertin | Date: | 2/7/19 |
| Organization: | Protection Professionals | Title: | Tech | Phone: | 207-775-5755 |
| The above ONLY pertains to the installation and testing of the 2 added notification devices in the unit, it does not constitute a full system test or inspection, this system and account belong to another vendor. |
| 12.3 Acceptance Test |
| Date and time of acceptance test: |  |
| Installing contractor representative: |  |
| Testing contractor representative: |  |
| Property representative: |  |
| AHJ representative: |  |