## Sheet1
FC901 Battery Calculations Worksheet |  | Fixed Field | Enter Numbers Here
ver. 1.3 |  | Calculated Field | Choose a value
2012-02-07
Ref. No
Submitted By
FC901 Panel |  | Standby (A) | Alarm (A)
Main Board |  | 0.178 | 0.203
Device Current Draw |  | 0.01984 | 0.01984
NAC 1 |  | 0 | 3
NAC 2 |  | 0
Aux power (external)
FCACity Tie |  |  |  |  | Yes | No
FSD901 Remote Annun. |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
Devices | Qty
HFP-11 / 8713
HFPO-11 / 8710
HFPT-11 / 8712
OOHC941
OOH941 | 3 | 0.00204 | 0.00204
OH921
OP921
HI921
FDCIO422 | 2 | 0.0024 | 0.0024
HMS / 8700-S/D/M
HTRI-S / 8702 | 11 | 0.0154 | 0.0154
HTRI-D / 8703
HTRI-R / 8704
HZM / 8705
HCP / 8706
ILED / 8726
Total | 16 | 0.01984 | 0.01984 | System OK
Total Current |  | 0.19784 | 3.2228
Standby Time | 24 | 4.7482 |  |  | Yes 1: 4; No 2: 24; No 3: 60
Alarm Time | 5 |  | 0.26857
AH required (no reserve) |  |  | 5.0167 |  | Yes 1: 5; No 2: 15; No 3: 30
Battery Reserve | 120% |  |  |  | Yes 1: 110%; No 2: 120%; No 3: 125%
AH Required (with reserve) |  |  | 6.0201 | System OK
Note on A9: Fixed value for all main board components
Note on A10: From device calculation below
Note on A11: Insert alarm current ONLY - supervision current included in the main board
Note on A12: Insert alarm current ONLY - supervisory current included in the main board
Note on A13: Don't include FSD current - that is calculated below!
Note on A14: Choose "Yes" if used
Note on A18: Note: 1.4 mA per device
Note on A19: Note: 1.4 mA per device
Note on A20: Note: 1.4 mA per device
Note on A21: Note: 0.75 mA per device
Note on A22: Note: 0.68 mA per device
Note on A23: Note: 0.30 mA per device
Note on A24: Note: 0.30 mA per device
Note on A25: Note: 0.28 mA per device
Note on A26: Note: 1.2 mA per device
Note on A27: Note: 1.4 mA per device
Note on A28: Note: 1.4 mA per device
Note on A29: Note: 1.4 mA per device
Note on A30: Note: 1.4 mA per device
Note on A31: Note: 1.4 mA per device
Note on A32: Note: 1.4 mA per device
Note on A33: Note: 1.4 mA per device
Note on A42: For battery aging