05P152

TO:       	Kandice S. Talbot – Planner

FROM:  	Jim Seymour – Development Review Coordinator, Sebago Technics, Inc.

# RE:       	Major Site Plan Review:  2nd Tee Business Park – 1039 Riverside LLC

# DATE:   	September 16, 2005

Sebago Technics has reviewed the revised submittal of the Major Site Plan application and supporting documentation dated July 2005 for the proposed redevelopment of seven (7) units at the originally approved site, and addition of 3(three) new units off of the former Douglas Brothers facility and current land owned by the Riverside Municipal Golf Course located at 1039 Riverside Street in the City of Portland.  We respectfully offer the following comments in outline format:

1.	Stormwater Management

Overall, the stormwater management plan and subsequent runoff quantity calculations appear to be acceptable and meet most of the requirements of both the MeDEP and the City of Portland.  We agree with the principle of “beating the peak” and thereby not requiring detention as long as all measures have been exhausted to treat the runoff to remove sediment and other pollutants. However, we have identified a few discrepancies that should be rectified prior to plan approval.

A. 	The project has not shown evidence that they meet the stormwater quality standard as required by the MeDEP and per the City’s stormwater standard for required treatment when parking areas exceed 25 spaces. A narrative and calculation discussing and showing proof that the standard has been met must be submitted for the entire site.

B.	The applicant states that the new entrance area will collect runoff from 0.18 acres and then will be treated with a water quality unit prior to discharging into the City drains in Riverside Street. No water quality unit is shown or described on the plans and the connection shall be made to the drain manhole not the catch basin. A drainage maintenance agreement will be required as well.

C.	The watershed #2 is diverting a great deal of increase flows to the City system, which doubles the rate of the existing condition rate. Is the City system capable or have capacity to handle the increase? Please obtain letter from Public Works acknowledging the ability to handle the increase. Increases to flows directed to the rear of the site are not of concern.

D.	We feel that the parking area associated with the existing warehouse has not adequately treated runoff and shall require another treatment unit between the last basin CB-21 and the outfall of the drainage to the ravine in the rear.

E.	We feel that the new entrance road adjacent to the golf course property shall be curbed with a Cape Cod style curb to direct runoff to the catch basins and eventually the treatment systems. Also the parking stalls on that property line for Unit15 shall also be curbed, guardrail or fenced to prevent parking up to the property line.

F. 	The water quality unit (WQU-#4) behind Unit 15, is an inaccessible area, and situated on a steep slope. We feel the unit shall be set at the location of DMH-9 and that DMH-9 may be eliminated. The outfall from this system shall require the appropriate apron/plunge pool design prior to exiting the property.

G.	Please indicate where all roof drain leaders will tie into the associated drain systems.

H. 	The watershed map is a little confusing in that some watersheds are not labeled correctly and the unit numbering uses the same symbol as the watershed delineation. Please refine and clean the plan so it is cleaner and easier to read.

2.	Road Access/Circulation

A.	Please refer to comments from the City Traffic Engineer for concerns of traffic movements, trip generation, and internal movements.

B. 	Where will access and parking be for Unit 9? No parking has been shown at this unit nor has a loading area.

C. 	 Will the site have directional signs? The site is interconnected, and locations and access to certain units confusing, how will the site be numbered/named and meet 911 Emergency Response address concerns?

3.	Utilities

A.	Letters to serve and available capacities appear to have been obtained showing that adequate service exists for the development.

B.	The electric services from Riverside Street shall be installed underground as should technically all electrical services since this plan appears to be a subdivision plan as well as a site plan. The overhead electrical service from pole #106 at the southern entrance exists, and is merely being replaced, which seems reasonable. The only other run of overhead utilities proposed is to service Unit 11 from behind Unit 5. Unit 5 was serviced with an overhead line, and the underground layout to the Unit 5 could conflict with water lines and be difficult given the topography. We would agree with overhead service to this unit if the poles and lines were set back away from the building on the ravine side of the proposed water so that they would be less obtrusive. This may require a waiver or modification of the standards.

4.	Grading & Erosion Controls

A.	The area proposed for outside of unit 13 exists as a gravel surface.  Surface runoff from this area sheet flows across the paving to Unit 10 and appears as though it will be a nuisance of sediment transfer, we recommend paving this gravel area. And for the gravel section i9n the rear of Unit 13, the applicant should consider providing a vegetated buffer to treat runoff, and/or stabilize the bank with erosion control matting and riprap.

B.	The entrance for access to Units 14 and 15 shall be constructed with a stabilized entrance.

C.	The toe of the slope in back of Unit 15 shall be protected with erosion   control measures and we recommend a double barrier at this location. The ditch along Unit 15 shall utilize check dams until vegetation is 90 % established, and given the slope the engineer may consider using Erosion control mesh to stabilize the soil in the ditch.

5.	Water Quality Treatment

A.	Per the City of Portland Technical and Design Standards and Guidelines, the applicant is required to treat stormwater runoff from parking facilities with 25 cars or more.  The existing warehouse parking area to the rear of Units 2 and 3 has 75 spaces, which appear to collect runoff and are not treated. As previously mentioned the site must conform to both the state’s Stormwater Law Chapter 500, and City ordinances for water quality. We strongly recommend a treatment unit for this parking area or proof that the entire site conforms to the water quality standard without this lot being treated.

B.	The sizing and detailed specifications with clear relativity to the water quality units shown on the plan shall be attached for review along with a site specific maintenance plan and draft contract for cleaning services. The submittal includes only one treatment unit’s details and the plan calls for two, the report implies three, and we feel a fourth may be needed.

6.	General

A.	A significant amount of wetlands were filled as a result of the original development and setbacks were established for the stream running across the parcel.  The plans appear to have not updated the newly acquired parcel for wetland delineation or potential setback from a stream. The Unit #15 is situated on a steep embankment. Is this part of the stream bank, or are there wetlands associated at the toe. Furthermore we recommend that a geotechnical report for the foundation be submitted for this unit during the building permit process to assure stability on the slope.

B.	The applicant is also required to file a revised Maine Construction General Permit for this project.  This must be obtained prior to the start of construction.

C.  	The plans shall provide a North arrow for reference.

D. 	The area delineated as snow storage behind Unit 5 is not appropriate or large enough for the entire site. The applicant has maximized available space for development and given the extent of parking, snow removal is of concern. Please provide a plan to address snow removal if it is to be stored on site.

E.	The general notes shall provide actual setbacks, parking requirements, and impervious ratios not just list the required zoning standards.

F.	The landscaping provisions appear rather limited and should be enhanced. The use of lower foundation plantings would enhance appearances as would lower vegetation along the Riverside building frontages and islands. Please delineate tree preserve areas and the measures that will be utilized to protect trees during construction. We strongly recommend that the City Arborist review the plans with recommendations.

Overall, the revised 1039 Riverside Street 2nd Tee Condominium Business Park project has been well planned out.  However, the applicant should make the necessary revisions, as noted in the above comments to conform to both MeDEP issues and Portland standards for water quality. Please contact our office if you have any questions.

JRS/jrs