03P200

TO:       	Kandice S. Talbot – Planner

FROM:  	Jim Seymour – Development Review Coordinator, Sebago Technics, Inc.

# RE:       	Major Site Plan Review:  Warehouse/Office Park – 1039 Riverside LLC

# DATE:   	February 6, 2004

Sebago Technics has reviewed the revised submittal of the Major Site Plan application and supporting documentation dated for the proposed development of nine (9) units at the site of the former Douglas Brothers facility located at 1039 Riverside Street in the City of Portland.  We respectfully offer the following comments in outline format:

1.	Stormwater Management

The stormwater management plan and subsequent calculations meet most of the requirements of both the MDEP and the City of Portland.  However, we have identified a few discrepancies that should be rectified prior to plan approval.

- There are several pipe slopes that do not meet typical engineering practices with regards to slope. Most pipe slopes within the City of Portland typically do not have slopes than 0.005 ft/ft. In circumstances with unusual elevation issues, lesser slopes are used but minimized.  Given the large elevation difference from the site surface to the outlet in the rear, we are not certain the extreme flat pipe slopes of 0.001 to 0.002 are necessary. The City has standards that require the pipe to maintain an average velocity of 3ft/sec. Many of the pipes are not modeled and some show the velocity is close but not obtained. We think at a minimum the pipe velocities need to be determined and if appropriate adjusted, to meet the City standards.

- Subcatchment 2 and 3 in the post-development scenario include a shared swale/ponding area, located in the front of the existing building.  The modeling plan indicates that the runoff will travel two separate ways, and uses the swale for each subcatchment. This is confusing and possibly a conflict with the model, that could impact runoff rates to either drainage system.  The swale area should be modeled as a pond and then shown to have two separate primary outlets (CB 9 and 12 inch culvert) This culvert shall be designed with inverts as well, cover issues could be a problem. Also the actual watershed areas may need to be re-analyzed or separated.

C.	The 36 in. stream culvert within the City Sewer Easement shall be riprapped with the appropriate stone size and dimensioning between the xisting 24 inch outlet pipe and 36 inch proposed pipe.

D.	The final treatment value calculations for the site shall be shown on the drawings along with the details for the proposed stormwater quality units. Also the necessary design criteria shall be included in the case a substitution is submitted the necessary design criteria are established.

E.	Due to the utilities and drainage infrastructure being shown on separate drawings it is difficult to conclude if there will be any pipe conflicts. Some areas appear to be relatively close. It shall be noted that a minimum of six-inch separation shall be attempted and that both storm and sewer shall have not less than three feet of cover. Some areas show insulation boards over the pipes to assist in frost protection for sewers, which is acceptable.

2.	Road Access/Circulation

- Chapter 14, Land Use, of the Code of Ordinances of the City of Portland requires    that the developer improve the abutting right-of-way with sidewalks and curbing.   Since there is granite curbing in this portion of Riverside Street, the applicant should provide the data of the curbing locations and sidewalk where it exists. Proper granite tipdowns and ramps shall be installed accordingly.

3.	Utilities

- The plans indicate that the units 6 thru 9 will utilize a water meter pit. It appears that the pit will be in conflict with catch basin 11 at the entrance.

- The plans shall provide the necessary utility easements for the power and telephone

Companies, to provide transformer pads

- The plan does not show gas service to be supplied to the development. Are there plans to exclude the site?  It appears that gas service could be an attribute to the site.

- The plan is a Subdivision Plan and under the ordinance the services must be underground. There are several electric services shown to be overhead. Also the electrical service is cut to the existing building and not shown reconnected.

- The fire hydrant located off the access street to serve the rear is located on the opposite side of the designed ditch. This is not practical or desired for the access during emergency situations.

- Will propane services be discontinued at the location of building 5 or relocated.

4.	Grading & Erosion Controls

- Level lipped spreaders shall be shown in detail and sized to handle the 25-year storm.

- There is a steep section of side slope along the 400 riverside street properties and Immucell Corp. property. This needs to be stabilized with riprap or other stabilizing fabric.

- All of the small parking islands and aisle ends shall be protected from turning vehicular traffic.  Curbing or other barriers shall be considered for green space protection.

- Last minute reconfiguration of the units 6 thru 9 created some drainage, utility, and grading conflicts against or around these units.  These revisions shall be reviewed once corrected to address grading and catch basins against the foundations.

- Some sections of the access road have steep sideslopes and shall consider guardrail.

5.	Details

The following details shall be included for review:

  - Dumpster enclosure details

  - Retaining wall details

  - Level lipped spreader

  - Double inlet catch basin.

  - 36 inch culvert installation and cross section

  - Stormwater treatment tanks

  - Casco traps

  - Paved entrance/landings sidewalk details

6.	General

Overall, the 1039 Riverside Street warehouse/office park project has a conceptually good layout/design.  However, the applicant should make the necessary revisions, as noted in the above comments.  Several technical details and issues need to be addressed prior to final approval. This may be acceptable if done by conditions. Given the comments we do not see the general layout altering, and given the last minute changes we will want to review all the necessary utility and grading revisions. We leave the final approval discretion with the Planning staff and Board.  Please contact our office if you have any questions.

JRS/jrs