## Sheet1
CERTIFICATE OF OCCUPANCY WALKTHROUGH PUNCH LIST
Allagash Distribution Warehouse - 21 Rice Street
2011-02-01
Item # | Description | Responsible | Status
1 | Electrical Panels - Make sure each panel has a label
2 | Electrical Panels - Type new panel schedules for each panel including the main panel
3 | Electrical Panels - Clean up the panel numbering in each panel (paint over existing markings)
4 | Electrical Panels - Install blank knock out cover in panel 1 at missing circuit breaker
5 | Electrical Panels - paint or mark the fire alarm circuit red in the panels
6 | Fire alarm panel - label the electrical circuit number/panel on the fire alarm panel
7 | Close up opening from loading dock into electrical room
8 | Install lock on electrical room door and label door "Electrical Room"
9 | Label sprinkler room door "Sprinkler Room"
10 | Wood Platform - Install additional headers to support the platform and bring down sprinkler heads for under the platform or remove the overhang back to the existing offices.
11 | Install 2 junction boxes and covers on open wires in ceiling in bay next to empty tank
12 | Electrical subpanel 3 - Install knock out seals on side of panel and cover hole on panel cover
13 | Install junction box cover on box located above two new loading dock levelers
14 | Install GFI outlet adjacent to bathroom sink or remove
15 | Fix light switch box at back entrance to office from the bay
16 | Remove or repair the two light switches labeled "Do not use light switches" adjacent to the offices
17 | Need certified sticker/label for fire alarm panel
18 | Install exit sign and emergency light above exit door adjacent to offices
19 | Install cover on light fixture above two new loading docks or remove fixture
Attached are the requirements for guards. This use, S-2, is allowed an exception to the 4" opening requirement. Openings here can not exceed 21" (IBC 1013.3(4)). Guards are also required at the non-loading side of the dock (IBC 1013.1 (1)). This is that area near the fork lift charger.
Also, provide a graspable handrail on each side of the stairs to the mezzanine in conformance with IBC 1012.
If you decide to retain the mezzanine over the old offices provide plans and calculations for the support.