## MS-9200UDLS
Note 1: You are fully responsible for verifying these calculations.
Note 2: Use the dropdowns and the yellow cells to enter values.
MS-9200UDLS Rev.3 Battery Calculation
Secondary Power Source Requirements | [10 empty] | 5 Minutes | 0.084 | 24 Hours | 24
[11 empty] | 10 Minutes | 0.167 | 48 Hours | 48
| Standby Current (amps) |  |  |  |  | Secondary Alarm Current (amps) |  |  |  |  | 15 Minutes | 0.25 | 60 Hours | 60
Device Type | Qty | Current Draw |  |  | Total | Qty | Current Draw |  |  | Total | 20 Minutes | 0.334 | 72 Hours | 72
Main Circuit Board | 1 | x | 0.145 | = | 0.145 | 1 | x | 0.275 | = | 0.275 | 25 Minutes | 0.417 | 90 Hours | 90
XRM-24B | 1 | x | 0 | = | 0 | 1 | x | 0 | = | 0 | 30 Minutes | 0.5
4XTMF | 0 | x | 0.005 | = |  | 0 | x | 0.011 | = |  | 45 Minutes | 0.75
IPDACT-2 | 0 | x | 0.093 | = |  | 0 | x | 0.136 | = |  | 60 Minutes | 1
IPDACT-2UD | 0 | x | 0.098 | = |  | 0 | x | 0.155 | =
ANN-BUS Devices
ANN-80(-W) | 2 | x | 0.015 | = | 0.03 | 2 | x | 0.04 | = | 0.08
ANN-LED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
ANN-RLED | 0 | x | 0.028 | = |  | 0 | x | 0.068 | =
ANN-RLY | 0 | x | 0.015 | = |  | 0 | x | 0.075 | =
ANN-I/O | 0 | x | 0.035 | = |  | 0 | x | 0.2 | =
ANN-S/PG | 0 | x | 0.045 | = |  | 0 | x | 0.045 | =
ACS Annunciators
ACM-8RF | 0 | x | 0.03 | = |  | 0 | x | 0.158 | =
ACM-16ATF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
ACM-32AF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
AEM-16ATF | 0 | x | 0.002 | = |  | 0 | x | 0.018 | =
AEM-32AF | 0 | x | 0.002 | = |  | 0 | x | 0.018 | =
AFM-16ATF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
AFM-32AF | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
AFM-16AF | 0 | x | 0.025 | = |  | 0 | x | 0.065 | =
LDM-32F | 0 | x | 0.04 | = |  | 0 | x | 0.056 | =
LDM-E32F | 0 | x | 0.002 | = |  | 0 | x | 0.018 | =
LCD-80F | 0 | x | 0.025 | = |  | 0 | x | 0.064 | =
Resettable Power
4-Wire Smoke Detectors | 0 | x | 0 | = |  | 0 | x | 0 | =
Addressable Devices
BEAM355 | 0 | x | 0.002 | =
BEAM355S | 0 | x | 0.002 | =
BEAM1224 | 0 | x | 0.017 | =
CP355 | 0 | x | 0.0003 | =
SD355 | 1 | x | 0.0003 | = | 0.0003
SD355T | 0 | x | 0.0003 | =
AD355 | 0 | x | 0.0003 | =
H355 | 0 | x | 0.0003 | =
H355R | 0 | x | 0.0003 | =
H355HT | 0 | x | 0.0003 | =
D350P | 0 | x | 0.0003 | =
D350RP | 0 | x | 0.0003 | =
D350PL | 0 | x | 0.0003 | =
D350RPL | 0 | x | 0.0003 | =
D355PL | 5 | x | 0.0003 | = | 0.0015
MMF-300 | 0 | x | 0.0004 | =
MMF-300-10 | 0 | x | 0.0035 | =
MDF-300 | 1 | x | 0.00075 | = | 0.00075
MMF-301 | 0 | x | 0.000375 | =
MMF-302 | 1 | x | 0.00027 | = | 0.00027
MMF-302-6 | 0 | x | 0.002 | =
BG-12LX | 11 | x | 0.0003 | = | 0.0033
CMF-300 | 0 | x | 0.00039 | =
CMF-300-6 | 0 | x | 0.00225 | =
CRF-300 | 0 | x | 0.00027 | =
CRF-300-6 | 0 | x | 0.00145 | =
I300 | 0 | x | 0.0004 | =
B501BH-2 | 0 | x | 0.001 | =
B501BHT-2 | 0 | x | 0.001 | =
B224RB | 0 | x | 0.0005 | =
B224BI | 0 | x | 0.00045 | =
B200SR | 0 | x | 0.0005 | =
CDRM-300 | 0 | x | 0.0013 | =
| Maximum alarm draw for all Addressable devices ---------------> | [8 empty] | 0.4
EOLR-1 | 0 | x | 0.02 | = |  | 0 | x | 0.02 | =
FCPS (Remote Sync) | [5 empty] | 0 | x | 0.0217 | =
Miscellaneous Device 1 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 2 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 3 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 4 | 0 | x | 0 | = |  | 0 | x | 0 | =
Miscellaneous Device 5 | 0 | x | 0 | = |  | 0 | x | 0 | =
NAC 1 | [5 empty] | 1 | x | 1.5 | = | 1.5
NAC 2 | [5 empty] | 1 | x | 1.5 | = | 1.5
NAC 3 | [5 empty] | 1 | x | 1.5 | = | 1.5
NAC 4 | [5 empty] | 1 | x | 1.5 | = | 1.5
Current Draw from TB3 |  |  | 0 | = |  |  |  | 0 | =
Total Standby Load |  |  |  |  | 0.18112 | Total Alarm Load |  |  |  | 6.755
MS-9200UDLS Rev.3 Battery Calculation
Calculation in Total Sheet
Required Standby Time in Hours
24 Hours
Standby Load Current |  |  | 0.18112 |  |  | x | 24 |  | = | 4.3469
Required Alarm Time in Minutes
5 Minutes
Alarm Load Current (Amps) |  |  | 6.755 |  |  | x | 0.084 |  | = | 0.56742
Total Current Load | [9 empty] | 4.9143
Multiply by the Derating Factor | [5 empty] | 1.2 |  |  | = | 1.2
Total Ampere Hours Required | [9 empty] | 5.8972
Recommended Batteries: | [5 empty] | BAT-1270 - 7AH Batteries
Battery Check
The batteries can be charged by the MS-9200UDLS Charger.
The batteries can be housed in the MS-9200UDLS Cabinet.
Current Draw Check
NAC#1 current is within the limitations of the circuit.
NAC#2 current is within the limitations of the circuit.
NAC#3 current is within the limitations of the circuit.
NAC#4 current is within the limitations of the circuit.
MS 9200UDLS Control Panel:
Output Current has exceeded panel limitations. Consider adding an Auxiliary Power Supply.
Note on H93: Select the Alarm Time in minutes from the dropdown list.
Note on H90: Select Standby Time in Hours from the dropdown list.
Note on H96: Select the Derating Factor from the dropdown list.
Note on B81: The total standby current must include both the nonresettable/resettable (TB1 Terminals 1 & 2) and resettable (TB1 Terminals 3 & 4) power. Caution must be taken to ensure that current drawn from these outputs during alarm does not exceed maximum ratings specified. Current limitations of TB3 & TB4 circuits is 2.5 amps per NAC Output and 1.0 amps per special application auxiliary power output.
Note on B77: Current limitation of Terminal TB3 & TB4 cirucits is 2.5 amps per NAC.
Note on B14: NOTE: There cannot be both ANN-BUS Devices and ACS Annunciators connected to the Control Panel. Choose ANN-BUS or ACS NOT both.
Note on B21: NOTE: There cannot be both ANN-BUS Devices and ACS Annunciators connected to the Control Panel. Choose ANN-BUS or ACS NOT both.
Note on J22: All eight ACM-8RF relays activated on a single module.
Note on J23: All annunciator LEDs on.
Note on J24: All annunciator LEDs on.
Note on J25: All annunciator LEDs on.
Note on J26: All annunciator LEDs on.
Note on J27: All annunciator LEDs on.
Note on J28: All annunciator LEDs on.
Note on J29: All annunciator LEDs on.
Note on J30: LDM-32F with LEDs on.
Note on J11: If using Reverse Polarity Alarm output, use 0.016; if using the Reverse Polarity Trouble output, use 0.021. Otherwise use 0.011.
Note on E34: Refer to the Device Compatibility Document for standby current.