## Sheet1
Fire System Sequence of Operations
Action
Actuation | Audio visual activation | Activate Audio/Visual signal at FACP & Ann | Device Desc. At FACP & Ann | Shutdown of HVAC Equip. | Log Events in System History | Silencing of Audible devices inclkuding FACP & Ann | Event Acknowledgement | Reset all system functions and visual devices | Transmission to Central Alarm Station A-Alarm T-Trouble S-Supervisory L-Log
Smoke Detectors in common area | X | X | X |  | X |  |  |  | A
Duct installed smoke detectors |  | X | X | X | X |  |  |  | S
Sprinkler flow switches | X | X | X |  | X |  |  |  | A
Sprinkler tamper switch |  | X | X |  | X |  |  |  | S
FACP/annunciator silence button |  | X | X |  | X |  | X |  | L
FACP/annunciator acknowledge button |  | X | X |  | X
FACP/annunciator reset button |  | X | X |  | X |  |  | X | L
Device Removals |  | X | X |  | X |  |  |  | T
Ground Faults |  | X | X |  | X |  |  |  | T
System wiring open |  | X | X |  | X |  |  |  | T
Power Loss |  | X | X |  | X |  |  |  | T
Back-up power loss |  | X | X |  | X |  |  |  | T
Communication Loss |  | X | X |  | X |  |  |  | T
Manual Pull Stations | X | X | X | X | X |  |  |  | A