From: 	Chris Pirone
To:	Jean Fraser
CC:	Danielle West-Chuhta
Date: 	2/26/2013 3:40 PM
Subject: 	Re: 1062 emergency response

I comfortable with this project moving forward as long as my original comments are met which were presented on 9/20/12. Please pay special attention to NFPA 1 2009 Fire Flow requirements not just the City Tech standards as these are more strict. Per the current plans more hydrants may need to be installed. 
 
Since this development is on City lines it is imperative that street addresses shall be approved by the City E-911 Addressing Officer before the certificate of occupancy will be issued which will make sure City of Portland Emergency Services are notified in case of an emergency.

Fire Comments:

All construction shall comply with City Code Chapter 10.
http://www.portlandmaine.gov/citycode/chapter010.pdf

Fire hydrants may be required based on 2009 NFPA 1.

Private fire mains and fire hydrants shall be maintained, tested and painted in accordance with Fire Department Regulations.
http://www.portlandmaine.gov/fireprevention/fdrulesandregulations.pdf

Street addresses shall be marked on the structure and shall be as approved by the City E-911 Addressing Officer. Contact Michelle Sweeney at 874-8682 for further information.

Sprinkler systems shall be installed in accordance with NFPA 13D
Captain Chris Pirone

Portland Fire Department
Fire Prevention Bureau
380 Congress Street
Portland, ME 04101
(t) 207.874.8405
(f) 207.874.8410
 
ü Please consider the environment before printing this email.