## Power Supply Config
|  |  | Project Name: |  | PORTLAND |  | Standby Hours: |  | 24
|  |  | Project ID: |  | FIRE BOAT QTRS |  | Alarm Mins: |  | 5
|  |  | Prepared By: |  | C.Lheureux |  | Derating Factor: |  | 1.2
5808 Calculations |  |  |  | Date: | 2013-07-24 |  | Voltage Drop Warning Threshold % :
Version 12.30.10 | [8 empty] | 10
Panel ID: | 5808 |  | Model: | 5808 Add. Fire Alarm Control Panel |  |  | Max NAC Current: |  | 3.0 Amps
Location: | MAIN ENTRY |  | Volts: | 24 VDC |  |  | Max Panel Current: |  | 6.0 Amps
Ckt.# | Circuit Name | Qty | Current Draw |  | Wire AWG | Ohms Per | Length(ft) | Actual | Volts @ | %Drop
|  |  | Standby | Alarm | & Type | 1000 Ft. | One-Way | Ohms | EOL
5808 | 5808 CTRL Panel | 1 | 0.17 | 0.325 | N/A
SK | Photo, Photo-T | 1 | 0.00027 | 0.00027
SK | Ion | 0 | 0 | 0
SK | Heat, Heat-HT | 0 | 0 | 0
SK | Heat ROR | 0 | 0 | 0
SK | Beam, Beam-T | 0 | 0 | 0
SK | Duct | 0 | 0 | 0
SK | Acclimate | 0 | 0 | 0
SK | Control | 0 | 0 | 0
SK | Relaymon | 0 | 0 | 0
SK | Control-6 | 0 | 0 | 0
SK | Monitor, Minimon | 1 | 0.000375 | 0.000375
SK | Monitor-2 | 3 | 0.00225 | 0.00225
SK | Monitor-10 | 0 | 0 | 0
SK | Pull-SA, Pull-DA | 2 | 0.00075 | 0.00075
SK | Relay | 0 | 0 | 0
SK | Relay-6 | 2 | 0.0029 | 0.0029
SK | Zone | 0 | 0 | 0
SK | Zone-6 | 0 | 0 | 0
SK | Isolator Module | 0 | 0 | 0
SSB224BI | Isolator Base | 0 | 0 | 0
B200SR | Sounder Base | 0 | 0 | 0
SSB224RB | Relay Base | 0 | 0 | 0
SSRTS151 | Magnetic Remote Test | 0 | 0 | 0
SSRTS151KEY | Key Activated Test | 0 | 0 | 0
SSRA100Z | Remote LED | 0 | 0 | 0
5860 | LCD Remote Annunc | 0 | 0 | 0
5824 | Serial/Parallel Module | 0 | 0 | 0
5496 | Power Expander | 0 | 0 | 0
5895XL | Power Expander | 0 | 0 | 0
5865-4 | LED Annunciator (4G) | 0 | 0 | 0
5865-3 | LED Annunciator (3G) | 0 | 0 | 0
5880 | LED Driver Module | 0 | 0 | 0
5883 | Relay Module | 0 | 0 | 0 | #14 Solid | 2.52 | 112 | 0.56448 | 20.0054 | 1.934%
NAC #1 | Notification Appl Circuit | 0.699 | 0 | 0.699 | #14 Stranded | 2.52 | 200 | 1.008 | 18.8406 | 7.644%
NAC #2 | Notification Appl Circuit | 1.547 | 0 | 1.547 | #14 Stranded | 2.52 | 200 | 1.008 | 19.0634 | 6.552%
NAC #3 | Notification Appl Circuit | 1.326 | 0 | 1.326 | #12 Solid | 1.59 |  | 0 | 20.4 | 0%
NAC #4 | Notification Appl Circuit | 0 | 0 | 0 | Total Alarm Current (Amps)
Total Standby Current (Amps) |  |  | 0.17655 | 3.9035 | Alarm Time In Minutes / 60 |  | (5 Mins)
Standby Time In Hours |  |  | 24 | 0.083333 | Total Alarm AH Required
Total Standby AH Required |  |  | 4.2371 | 0.3253 | Command Shortcuts
Total Combined AH Required |  |  | 4.5624
Multiply By The Derating Factor |  |  | 1.2
Minimum Battery AmpHours Required |  |  | 5.4749
Note on F26: The SK-Beam-T draws a maximum of 500 mA from auxiliary power only when the test feature is used. This should be considered when determining auxiliary power capacity but not calculated into current requirements for day to day operation.
Note on G26: The SK-Beam-T draws a maximum of 500 mA from auxiliary power only when the test feature is used. This should be considered when determining auxiliary power capacity but not calculated into current requirements for day to day operation.
Note on F38: Auxiliary power standby draw is 12 mA per SK-Zone module. You will need to add this draw to the auxiliary power you are using.
Note on G38: Auxiliary power alarm draw is 90 mA per SK-Zone module. You will need to add this draw to the auxiliary power you are using.
Note on F39: Auxiliary power standby draw is 50 mA per SK-Zone-6 module. You will need to add this draw to the auxiliary power you are using.
Note on G39: Auxiliary power alarm draw is 270 mA per SK-Zone-6 module. You will need to add this draw to the auxiliary power you are using.
Note on F42: Auxiliary power standby draw is .5 mA per sounder base. You will need to add this draw to the auxiliary power you are using.
Note on G42: Auxiliary power alarm draw is 35 mA per sounder base. You will need to add this draw to the auxiliary power you are using.
Note on F29: Auxiliary power standby draw is 1.7 mA per SK-Control module. You will need to add this draw to the auxiliary power you are using.
Note on G29: Auxiliary power alarm draw is 7 mA per SK-Control module. You will need to add this draw to the auxiliary power you are using.
Note on F31: Auxiliary power standby draw is 8 mA per SK-Control-6 module. You will need to add this draw to the auxiliary power you are using.
Note on G31: Auxiliary power alarm draw is 20 mA per SK-Control-6 module. You will need to add this draw to the auxiliary power you are using.
Note on F27: Current draw is the same when using the SK-PHOTO or SK-PHOTOR smoke head with the SK-DUCT.
Note on G27: Current draw is the same when using the SK-PHOTO or SK-PHOTOR smoke head with the SK-DUCT.

## Smokes
Device Database
Device Database
Command Shortcuts
| Item# | Device / Description | Current Draw In Amperes
|  |  | Standby | *Alarm
| 1 | Unused
| 2 | Gentex GCC24 Horn/Strobe (15cd) | 0 | 0.143
| 3 | Gentex GCC24 Horn/Strobe (30cd) | 0 | 0.153
| 4 | Gentex GCC24 Horn/Strobe (75cd) | 0 | 0.27
| 5 | Gentex GCC24 Horn/Strobe (95cd) | 0 | 0.341
| 6 | Gentex GCC24 Horn/Strobe (115cd) | 0 | 0.383
| 7 | Gentex GCC24 Horn/Strobe (150cd) | 0 | 0.477
| 8 | Gentex GCS24 Strobe (15cd) | 0 | 0.12
| 9 | Gentex GCS24 Strobe (30cd) | 0 | 0.13
| 10 | Gentex GCS24 Strobe (75cd) | 0 | 0.247
| 11 | Gentex GCS24 Strobe (95cd) | 0 | 0.318
| 12 | Gentex GCS24 Strobe (115cd) | 0 | 0.36
| 13 | Gentex GCS24 Strobe (150cd) | 0 | 0.454
| 14 | Gentex GEC324 Horn/Strobe (15cd) | 0 | 0.134
| 15 | Gentex GEC324 Horn/Strobe (30cd) | 0 | 0.152
| 16 | Gentex GEC324 Horn/Strobe (60cd) | 0 | 0.193
| 17 | Gentex GEC324 Horn/Strobe (75cd) | 0 | 0.236
| 18 | Gentex GEC324 Horn/Strobe (110cd) | 0 | 0.28
| 19 | Gentex GES324 Strobe (15cd) | 0 | 0.078
| 20 | Gentex GES324 Strobe (30cd) | 0 | 0.096
| 21 | Gentex GES324 Strobe (60cd) | 0 | 0.137
| 22 | Gentex GES324 Strobe (75cd) | 0 | 0.18
| 23 | Gentex GES324 Strobe (110cd) | 0 | 0.224
| 24 | Gentex GEC24 Horn/Strobe (15cd) | 0 | 0.133
| 25 | Gentex GEC24 Horn/Strobe (30cd) | 0 | 0.151
| 26 | Gentex GEC24 Horn/Strobe (60cd) | 0 | 0.192
| 27 | Gentex GEC24 Horn/Strobe (75cd) | 0 | 0.235
| 28 | Gentex GEC24 Horn/Strobe (110cd) | 0 | 0.279
| 29 | Gentex GEC24 Horn/Strobe (177cd) | 0 | 0.343
| 30 | Gentex GEH24 Horn | 0 | 0.056
| 31 | Gentex GES24 Strobe (15cd) | 0 | 0.078
| 32 | Gentex GES24 Strobe (30cd) | 0 | 0.096
| 33 | Gentex GES24 Strobe (60cd) | 0 | 0.137
| 34 | Gentex GES24 Strobe (75cd) | 0 | 0.18
| 35 | Gentex GES24 Strobe (110cd) | 0 | 0.224
| 36 | Gentex GES24 Strobe (177cd) | 0 | 0.288
| 37 | Gentex GX91 Mini-Horn (Continuous) | 0 | 0.015
| 38 | Gentex GX93 Mini-Horn (Temporal) | 0 | 0.022
| 39 | Gentex WGE Strobe (75cd) | 0 | 0.18
| 40 | Gentex WGEC Horn/Strobe (75cd) | 0 | 0.236
| 41 | Silent Knight end of line relay EOL-1224RLY | 0.015 | 0.015
| 42 | System Sensor CH Chime | 0 | 0.054
| 43 | System Sensor CHS Chime/Stobe (15cd) | 0 | 0.07
| 44 | System Sensor CHS Chime/Stobe (15/75cd) | 0 | 0.081
| 45 | System Sensor CHS Chime/Strobe (30cd) | 0 | 0.099
| 46 | System Sensor CHS Chime/Strobe (75cd) | 0 | 0.165
| 47 | System Sensor CHS Chime/Strobe (95cd) | 0 | 0.189
| 48 | System Sensor CHS Chime/Strobe (110cd) | 0 | 0.21
| 49 | System Sensor CHS Chime/Strobe (115cd) | 0 | 0.217
| 50 | System Sensor HR/HRK/HW Horn | 0 | 0.069
| 51 | System Sensor MH Mini-Horn | 0 | 0.029
| 52 | System Sensor P2/PC2 Horn/Strobe (15cd) | 0 | 0.091
| 53 | System Sensor P2/PC2 Horn/Strobe (15/75cd) | 0 | 0.1
| 54 | System Sensor P2/PC2 Horn/Strobe (30cd) | 0 | 0.116
| 55 | System Sensor P2/PC2 Horn/Strobe (75cd) | 0 | 0.176
| 56 | System Sensor P2/PC2 Horn/Strobe (95cd) | 0 | 0.201
| 57 | System Sensor P2/PC2 Horn/Strobe (110cd) | 0 | 0.221
| 58 | System Sensor P2/PC2 Horn/Strobe (115cd) | 0 | 0.229
| 59 | System Sensor P2/PC2 Horn/Strobe (135cd) | 0 | 0.255
| 60 | System Sensor P2/PC2 Horn/Strobe (150cd) | 0 | 0.27
| 61 | System Sensor P2/PC2 Horn/Strobe (177cd) | 0 | 0.302
| 62 | System Sensor P2/PC2 Horn/Strobe (185cd) | 0 | 0.309
| 63 | System Sensor S/SC Strobe (15cd) | 0 | 0.066
| 64 | System Sensor S/SC Strobe (15/75cd) | 0 | 0.077
| 65 | System Sensor S/SC Strobe (30cd) | 0 | 0.094
| 66 | System Sensor S/SC Strobe (75cd) | 0 | 0.158
| 67 | System Sensor S/SC Strobe (95cd) | 0 | 0.181
| 68 | System Sensor S/SC Strobe (110cd) | 0 | 0.202
| 69 | System Sensor S/SC Strobe (115cd) | 0 | 0.21
| 70 | System Sensor S/SC Strobe (135cd) | 0 | 0.228
| 71 | System Sensor S/SC Strobe (150cd) | 0 | 0.246
| 72 | System Sensor S/SC Strobe (177cd) | 0 | 0.281
| 73 | System Sensor S/SC Strobe (185cd) | 0 | 0.286
| 74 | Wheelock AH24 Horn | 0 | 0.08
| 75 | Wheelock AS241575 Horn/Strobe (1575cd) | 0 | 0.201
| 76 | Wheelock AS24MCW Horn/Strobe (15cd) | 0 | 0.168
| 77 | Wheelock AS24MCW Horn/Strobe (30cd) | 0 | 0.205
| 78 | Wheelock AS24MCW Horn/Strobe (75cd) | 0 | 0.28
| 79 | Wheelock AS24MCW Horn/Strobe (110cd) | 0 | 0.347
| 80 | Wheelock AS24MCWH Horn/Strobe (135cd) | 0 | 0.435
| 81 | Wheelock AS24MCWH Horn/Strobe (185cd) | 0 | 0.56
| 82 | Wheelock AS24MCC Horn/Strobe (15cd) | 0 | 0.175
| 83 | Wheelock AS24MCC Horn/Strobe (30cd) | 0 | 0.218
| 84 | Wheelock AS24MCC Horn/Strobe (75cd) | 0 | 0.301
| 85 | Wheelock AS24MCC Horn/Strobe (95cd) | 0 | 0.365
| 86 | Wheelock AS24MCCH Horn/Strobe (115cd) | 0 | 0.435
| 87 | Wheelock AS24MCCH Horn/Strobe (177cd) | 0 | 0.56
| 88 | Wheelock CH70 Chime | 0 | 0.022
| 89 | Wheelock CH70241575 Chime/Strobe (1575cd) | 0 | 0.112
| 90 | Wheelock CH7024MCW Chime/Strobe (15cd) | 0 | 0.082
| 91 | Wheelock CH7024MCW Chime/Strobe (30cd) | 0 | 0.114
| 92 | Wheelock CH7024MCW Chime/Strobe (75cd) | 0 | 0.187
| 93 | Wheelock CH7024MCW Chime/Strobe (110cd) | 0 | 0.242
| 94 | Wheelock CH7024MCWH Chime/Strobe (135cd) | 0 | 0.322
| 95 | Wheelock CH7024MCWH Chime/Strobe (185cd) | 0 | 0.442
| 96 | Wheelock CH90 Chime | 0 | 0.022
| 97 | Wheelock CH9024MCC Chime/Strobe (15cd) | 0 | 0.087
| 98 | Wheelock CH9024MCC Chime/Strobe (30cd) | 0 | 0.127
| 99 | Wheelock CH9024MCC Chime/Strobe (75cd) | 0 | 0.211
| 100 | Wheelock CH9024MCC Chime/Strobe (95cd) | 0 | 0.271
| 101 | Wheelock CH9024MCCH Chime/Strobe (115cd) | 0 | 0.322
| 102 | Wheelock CH9024MCCH Chime/Strobe (177cd) | 0 | 0.442
| 103 | Wheelock HS24 Horn | 0 | 0.11
| 104 | Wheelock HS24MCC Horn/Strobe (15cd) | 0 | 0.175
| 105 | Wheelock HS24MCC Horn/Strobe (30cd) | 0 | 0.215
| 106 | Wheelock HS24MCC Horn/Strobe (75cd) | 0 | 0.299
| 107 | Wheelock HS24MCC Horn/Strobe (95cd) | 0 | 0.359
| 108 | Wheelock HS24MCCH Horn/Strobe (115cd) | 0 | 0.41
| 109 | Wheelock HS24MCCH Horn/Strobe (177cd) | 0 | 0.53
| 110 | Wheelock HS4241575W Horn/Strobe (1575cd) | 0 | 0.2
| 111 | Wheelock HS424MCW Horn/Strobe (15cd) | 0 | 0.17
| 112 | Wheelock HS424MCW Horn/Strobe (30cd) | 0 | 0.202
| 113 | Wheelock HS424MCW Horn/Strobe (75cd) | 0 | 0.275
| 114 | Wheelock HS424MCW Horn/Strobe (110cd) | 0 | 0.33
| 115 | Wheelock HS424MCWH Horn/Strobe (135cd) | 0 | 0.41
| 116 | Wheelock HS424MCWH Horn/Strobe (185cd) | 0 | 0.53
| 117 | Wheelock MT24 Multitone Appliance | 0 | 0.142
| 118 | Wheelock MT241575 Multitone/Strobe (1575cd) | 0 | 0.232
| 119 | Wheelock MTWP2475 Multitone/Strobe (180cd) | 0 | 0.28
| 120 | Wheelock MT24MCW Multitone/Strobe (15cd) | 0 | 0.202
| 121 | Wheelock MT24MCW Multitone/Strobe (30cd) | 0 | 0.234
| 122 | Wheelock MT24MCW Multitone/Strobe (75cd) | 0 | 0.307
| 123 | Wheelock MT24MCW Multitone/Strobe (110cd) | 0 | 0.362
| 124 | Wheelock NH24 Horn | 0 | 0.044
| 125 | Wheelock NS241575W Horn/Strobe (1575cd) | 0 | 0.148
| 126 | Wheelock NS24MCW Horn/Strobe (15cd) | 0 | 0.118
| 127 | Wheelock NS24MCW Horn/Strobe (30cd) | 0 | 0.151
| 128 | Wheelock NS24MCW Horn/Strobe (75cd) | 0 | 0.228
| 129 | Wheelock NS24MCW Horn/Strobe (110cd) | 0 | 0.288
| 130 | Wheelock NS24MCC Horn/Strobe (15cd) | 0 | 0.126
| 131 | Wheelock NS24MCC Horn/Strobe (30cd) | 0 | 0.168
| 132 | Wheelock NS24MCC Horn/Strobe (75cd) | 0 | 0.253
| 133 | Wheelock NS24MCC Horn/Strobe (95cd) | 0 | 0.319
| 134 | Wheelock NS24MCCH Horn/Strobe (115cd) | 0 | 0.394
| 135 | Wheelock NS24MCCH Horn/Strobe (177cd) | 0 | 0.521
| 136 | Wheelock RSS/RSSP241575W Strobe (1575cd) | 0 | 0.09
| 137 | Wheelock RSS/RSSP24MCW Strobe (15cd) | 0 | 0.06
| 138 | Wheelock RSS/RSSP24MCW Strobe (30cd) | 0 | 0.092
| 139 | Wheelock RSS/RSSP24MCW Strobe (75cd) | 0 | 0.165
| 140 | Wheelock RSS/RSSP24MCW Strobe (110cd) | 0 | 0.22
| 141 | Wheelock RSS/RSSP24MCWH Strobe (135cd) | 0 | 0.3
| 142 | Wheelock RSS/RSSP24MCWH Strobe (185cd) | 0 | 0.42
| 143 | Wheelock RSS/RSSP24MCC Strobe (15cd) | 0 | 0.065
| 144 | Wheelock RSS/RSSP24MCC Strobe (30cd) | 0 | 0.105
| 145 | Wheelock RSS/RSSP24MCC Strobe (75cd) | 0 | 0.189
| 146 | Wheelock RSS/RSSP24MCC Strobe (95cd) | 0 | 0.249
| 147 | Wheelock RSS/RSSP24MCCH Strobe (115cd) | 0 | 0.3
| 148 | Wheelock RSS/RSSP24MCCH Strobe (177cd) | 0 | 0.42
| 149 | Silent Knight SD500-ANM Notification Module | 0.008 | 0.06
| 150 | Silent Knight SD500-LED LED Module | 0.01 | 0.22
| 151 | Silent Knight SD500-SDM Smoke Det Module | 0.02 | 0.106
| 152 | Silent Knight SD505-6SB Sounder Base | 0.001 | 0.032
| 153 | Silent Knight SD505-DUCTR Duct w/Relay | 0.02 | 0.062
| 154 | User Defined
| 155 | User Defined
| 156 | User Defined
| 157 | User Defined
| 158 | User Defined
| 159 | User Defined
| 160 | User Defined
| 161 | User Defined
| 162 | User Defined
*Alarm draws are listed as worse case. Consult manufacturer's specification sheet for actual alarm draw with the candela and/or horn mode you are using.
All of the devices shown in this table will appear as choices in the dropdown boxes used to configure each circuit. To add new devices: Scroll down and replace any of the user defined entries with the information of the device you wish to add to the list of choices.

## Circuit Config
Circuit Configuration
Project Name: | PORTLAND | Project ID: |  | FIRE BOAT QTRS | Alarm Mins:
Prepared By: | C.Lheureux | Date: |  | 2013-07-24 | Voltage Drop Warning Threshold % :
Ckt. Number: | NAC 1 Community Building | Panel ID: | 5808
Ckt. Name: | Notification Appl Circuit | Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
2 | System Sensor P2/PC2 Horn/Strobe (30cd) | 0 | 0.116 | 0 | 0.232 | 54
3 | System Sensor S/SC Strobe (15cd) | 0 | 0.066 | 0 | 0.198 | 63
2 | System Sensor P2/PC2 Horn/Strobe (15cd) | 0 | 0.091 | 0 | 0.182 | 52
3 | System Sensor MH Mini-Horn | 0 | 0.029 | 0 | 0.087 | 51
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0.699
Ckt. Number: | NAC #2 | Panel ID: | 5808
Ckt. Name: | Notification Appl Circuit | Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
7 | System Sensor P2/PC2 Horn/Strobe (110cd) | 0 | 0.221 | 0 | 1.547 | 57
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 1.547
Ckt. Number: | NAC #3 | Panel ID: | 5808
Ckt. Name: | Notification Appl Circuit | Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
6 | System Sensor P2/PC2 Horn/Strobe (110cd) | 0 | 0.221 | 0 | 1.326 | 57
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 1.326
Ckt. Number: | NAC #4 | Panel ID: | 5808
Ckt. Name: | Notification Appl Circuit | Use:
Qty | Device | Current Draw Each |  | Current Draw Total
|  | Standby | Alarm | Standby | Alarm
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
| Unused | 0 | 0 | 0 | 0 | 1
|  |  |  | 0 | 0
|  |  | Totals | 0 | 0

## Devices (hidden)
Device Database
Notification Appliance Database
Item# | Device / Description | Current Draw In Amperes
|  | Standby | Alarm
1 | Unused
2 | Gentex GMH-24-X Horn | 0 | 0.038
3 | Gentex GX90-4 Horn | 0 | 0.015
4 | Gentex GX90S-4-15 Horn | 0 | 0.093
5 | Gentex GX90S-4-1575 Horn | 0 | 0.108
6 | Gentex GXS-4-1575 Strobe | 0 | 0.145
7 | Gentex HG124 Horn | 0 | 0.03
8 | Gentex HS24-110 Horn/Strobe | 0 | 0.14
9 | Gentex HS24-15 Horn/Strobe | 0 | 0.077
10 | Gentex HS24-15/75 Horn/Strobe | 0 | 0.087
11 | Gentex HS24-30 Horn/Strobe | 0 | 0.087
12 | Gentex HS24-60 Horn/Strobe | 0 | 0.114
13 | Gentex HS24-75 Horn/Strobe | 0 | 0.116
14 | Gentex SHG24-110 Horn/Strobe | 0 | 0.25
15 | Gentex SHG24-15/75-C Horn/Strobe | 0 | 0.123
16 | Gentex SHG24-15/75-W Horn/Strobe | 0 | 0.123
17 | Gentex SHG24-15/75-Z Horn/Strobe | 0 | 0.123
18 | Gentex SHG24-30 Horn/Strobe | 0 | 0.123
19 | Gentex SHG24-30/75 Horn/Strobe | 0 | 0.172
20 | Gentex SHG24-60 Horn/Strobe | 0 | 0.145
21 | Gentex ST24-110 Strobe | 0 | 0.11
22 | Gentex ST24-15 Strobe | 0 | 0.047
23 | Gentex ST24-15/75 Strobe | 0 | 0.057
24 | Gentex ST24-30 Strobe | 0 | 0.057
25 | Gentex ST24-60 Strobe | 0 | 0.084
26 | Gentex ST24-75 Strobe | 0 | 0.086
27 | Silent Knight end of line relay EOL-1224RLY | 0.015 | 0.015
28 | System Sensor H12/24 Horn | 0 | 0.025
29 | System Sensor P24110 Horn/Strobe | 0 | 0.165
30 | System Sensor P241575 Horn/Strobe | 0 | 0.074
31 | System Sensor P2430 Horn/Strobe | 0 | 0.092
32 | System Sensor P2475 Horn/Strobe | 0 | 0.148
33 | System Sensor S2415 Strobe | 0 | 0.043
34 | System Sensor S241575 Strobe | 0 | 0.049
35 | System Sensor S2430 Strobe | 0 | 0.067
36 | System Sensor S2475 Strobe | 0 | 0.123
37 | System Sensor SS24110 Strobe | 0 | 0.14
38 | Wheelock AMT-24-IS-VFR Strobe Horn | 0 | 0.04
39 | Wheelock AMT-24-LSM-VFR Strobe Horn | 0 | 0.125
40 | Wheelock AS-24110-HFR Strobe Horn | 0 | 0.202
41 | Wheelock AS-241575-VFR Strobe Horn | 0 | 0.102
42 | Wheelock AS-2415-VFR Strobe Horn | 0 | 0.087
43 | Wheelock AS-2430-VFR Strobe Horn | 0 | 0.135
44 | Wheelock AS-2475-VFR Strobe Horn | 0 | 0.156
45 | Wheelock MIZ-24-R Mini-Horn | 0 | 0.012
46 | Wheelock MIZ-24-W Mini-Horn | 0 | 0.012
47 | User Defined
48 | User Defined
49 | User Defined
50 | User Defined
51 | User Defined
52 | User Defined
53 | User Defined
54 | User Defined
55 | User Defined
56 | User Defined
57 | User Defined
58 | User Defined
59 | User Defined
60 | User Defined
61 | User Defined
62 | User Defined
63 | User Defined
64 | User Defined
65 | User Defined
66 | User Defined
67 | User Defined
68 | User Defined
69 | User Defined
70 | User Defined
71 | User Defined
72 | User Defined
73 | User Defined
74 | User Defined
75 | User Defined
76 | User Defined
77 | User Defined
78 | User Defined
79 | User Defined
80 | User Defined
81 | User Defined
82 | User Defined
83 | User Defined
84 | User Defined
85 | User Defined
86 | User Defined
87 | User Defined
88 | User Defined
89 | User Defined
90 | User Defined
91 | User Defined
92 | User Defined
93 | User Defined
94 | User Defined
95 | User Defined
96 | User Defined
97 | User Defined
98 | User Defined
99 | User Defined
100 | User Defined
101 | User Defined
102 | User Defined
103 | User Defined
104 | User Defined
105 | User Defined
106 | User Defined
107 | User Defined
108 | User Defined
109 | User Defined
110 | User Defined
111 | User Defined
112 | User Defined
113 | User Defined
114 | User Defined
115 | User Defined
116 | User Defined
117 | User Defined
118 | User Defined
119 | User Defined
120 | User Defined
121 | User Defined
122 | User Defined
123 | User Defined
124 | User Defined
125 | User Defined
126 | User Defined
127 | User Defined
128 | User Defined
129 | User Defined
130 | User Defined
131 | User Defined
132 | User Defined
133 | User Defined
134 | User Defined
135 | User Defined
136 | User Defined
137 | User Defined
138 | User Defined
139 | User Defined
140 | User Defined
141 | User Defined
142 | User Defined
143 | User Defined
144 | User Defined
145 | User Defined
146 | User Defined
147 | User Defined
148 | User Defined
149 | User Defined
150 | User Defined
All of the devices shown in this table will appear as choices in the dropdown boxes used to configure each NAC circuit. To add new devices: Scroll down and replace any of the user defined entries with the information of the device you wish to add to the list of choices.
Command Shortcuts

## Data (hidden)
Conductor Properties NEC Chap. 9
Item | Wire Type | Ohms Per 1000 ft.
1 | #12 Solid | 1.59
2 | #12 Stranded | 1.59
3 | #14 Solid | 2.52
4 | #14 Stranded | 2.52
5 | #16 Solid | 4.02
6 | #16 Stranded | 4.02
7 | #18 Solid | 6.39
8 | #18 Stranded | 6.39
Cell Links For The Wire Type Drop Down Boxes Associated With Each 5395
| 5395(1) | 5395(2) | 5395(3) | 5395(4) | 5395(5) | 5395(6) | 5395(7) | 5395(8)
1 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2 | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
3 | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1
4 | bar: 5395(1) to 5395(8)
5 | bar: 5395(1) to 5395(8)
6 | bar: 5395(1) to 5395(8)
1 | 5395(1): Notification Appl Circuit
2 | 5395(1): Aux Power Circuit
3 | 5395(1): Aux Power Circuit
| I/O1 | 1
| I/O2 | 1
| I/O3 | 1
| I/O4 | 1
| I/O5 | 1
| I/O6 | 1